## Bus
Bus Data | Energinet.dk | 2020
Bus Index | Bus Name | Station Full Name | Location Name | Voltage base[kV] | Voltage min[pu] | Voltage max[pu]
0 | MRP_132_S1 |  | SVERIGE | 132 | 0 | 1.05
1 | MRP_132_S2 |  | SVERIGE | 132 | 0 | 1.05
2 | SÅN_400_S1 |  | SVERIGE | 400 | 0 | 1.05
3 | SÅN_400_S2 |  | SVERIGE | 400 | 0 | 1.05
4 | BA2_150_SFIK |  | TYSKLAND | 150 | 0 | 1.05
5 | BWT_400_SFIK |  | TYSKLAND | 150 | 0 | 1.05
6 | FLE_400_SFIK |  | TYSKLAND | 400 | 0 | 1.05
7 | JARD400_SFIK |  | TYSKLAND | 400 | 0 | 1.05
8 | NBL_400_S1 |  | TYSKLAND | 400 | 0 | 1.05
9 | UCTE_400_SFIK |  | TYSKLAND | 400 | 0 | 1.05
11 | term_CO1_XED_EE1D | HVDC STATION COBRA POL 1 | dcCO | 400 | 0 | 1.05
12 | term_KO1_XBE_BJ1K | HVDC STATION KONTEK POL 2 | dcKO | 400 | 0 | 1.05
13 | term_KS1_XVH_ST31 | HVDC STATION KONTISKAN POL 1 | dcKS | 400 | 0 | 1.05
14 | term_KS2_XVH_LI11 | HVDC STATION KONTISKAN POL 2 | dcKS | 400 | 0 | 1.05
15 | term_SB1_XFG_HK11 | HVDC STATION STOREBÆLT POL 1 | dcSB | 400 | 0 | 1.05
16 | term_SB1_XFG_HK12 | HVDC STATION STOREBÆLT POL 1 | dcSB | 400 | 0 | 1.05
17 | term_SK1_XTJ_K13K | HVDC STATION SKAGERAK POL 1 | dcSK | 165 | 0 | 1.05
18 | term_SK2_XTJ_K23K | HVDC STATION SKAGERAK POL 2 | dcSK | 165 | 0 | 1.05
19 | term_SK3_XTJ_K31K | HVDC STATION SKAGERAK POL 3 | dcSK | 400 | 0 | 1.05
20 | term_SK4_XTJ_K41K | HVDC STATION SKAGERAK POL 3 | dcSK | 400 | 0 | 1.05
21 | UWN_150_SS1 | 150 kV STATION UMSPANNWERK NORD | FLENSBORG | 165 | 0.88 | 1.03
22 | XBI_R11_K |  | Fictitious Border Node | 400 | 0 | 9999
24 | XBW_BJ1K |  | Fictitious Border Node | 400 | 0 | 1.05
25 | XDE_DS11 |  | Fictitious Border Node | 150 | 0 | 1.05
26 | XDE_DS12 |  | Fictitious Border Node | 150 | 0 | 1.05
27 | XED_EE1D |  | Fictitious Border Node | 400 | 0 | 1.05
29 | XFG_HK11 |  | Fictitious Border Node | 400 | 0 | 1.05
30 | XFG_HK12 |  | Fictitious Border Node | 400 | 0 | 1.05
31 | XFL_KA11 |  | Fictitious Border Node | 400 | 0 | 1.05
32 | XFL_KA12 |  | Fictitious Border Node | 400 | 0 | 1.05
33 | XJA_KA11 |  | Fictitious Border Node | 400 | 0 | 1.05
34 | XJA_KA12 |  | Fictitious Border Node | 400 | 0 | 1.05
35 | XMO_TE31 |  | Fictitious Border Node | 132 | 0 | 1.05
36 | XMO_TE32 |  | Fictitious Border Node | 132 | 0 | 1.05
37 | XNI_ED11 |  | Fictitious Border Node | 400 | 0 | 9999
38 | XNI_ED12 |  | Fictitious Border Node | 400 | 0 | 9999
39 | XSA_GO11 |  | Fictitious Border Node | 400 | 0 | 1.05
40 | XSA_HO11 |  | Fictitious Border Node | 400 | 0 | 1.05
41 | XTJ_K13K |  | Fictitious Border Node | 165 | 0 | 1.05
43 | XTJ_K23K |  | Fictitious Border Node | 165 | 0 | 1.05
45 | XTJ_K31K |  | Fictitious Border Node | 400 | 0 | 1.05
47 | XTJ_K41K |  | Fictitious Border Node | 400 | 0 | 1.05
49 | XVH_L11K |  | Fictitious Border Node | 400 | 0 | 1.05
51 | XVH_L21K |  | Fictitious Border Node | 400 | 0 | 1.05
53 | ALL_132_F1 | 132 KV STATION ALLERØDGÅRD | ENDKE | 132 | 0.95 | 1.1
54 | AMF_132_F | Amager Forbrænding | ENDKE | 132 | 0 | 1.05
55 | AMK_132_A | 132 KV STATION AMAGER KBST | ENDKE | 132 | 0.95 | 1.05
56 | AMV_010_SFIK | Amagerværket | ENDKE | 10 | 0.95 | 1.05
57 | AMV_0173_SFIK | Amagerværket | ENDKE | 17 | 0.95 | 1.05
58 | AMV_132_A | 132 KV STATION AMAGERVÆRKET | ENDKE | 132 | 0.95 | 1.05
59 | ASV_0122_SFIK | ASNÆSVÆRKET | ENDKE | 12 | 0.95 | 1.05
60 | ASV_0215_SFIK | ASNÆSVÆRKET | ENDKE | 21 | 0.95 | 1.05
61 | ASV_132_F | 132 KV STATION ASNÆSVÆRKET | ENDKE | 132 | 0.95 | 1.05
62 | ASV_4001_SFIK | 400 KV STATION ASNÆSVÆRKET | ENDKE | 400 | 0.95 | 1.05
63 | ASV_400_K | 400 KV STATION ASNÆSVÆRKET | ENDKE | 400 | 0.95 | 1.05
64 | AVV_0122_SFIK | AVEDØREVÆRKET | ENDKE | 11.5 | 0.87 | 1.13
65 | AVV_0123_SFIK | AVEDØREVÆRKET | ENDKE | 11.5 | 0.87 | 1.13
66 | AVV_0171_SFIK | AVEDØREVÆRKET | ENDKE | 17 | 0.95 | 1.05
67 | AVV_0201_SFIK | AVEDØREVÆRKET | ENDKE | 19.5 | 0.92 | 1.08
68 | AVV_132_F | 132 KV STATION AVEDØREVÆRKET | ENDKE | 132 | 0.95 | 1.05
69 | AVV_132_SFIK | 132 KV STATION AVEDØREVÆRKET | ENDKE | 132 | 0.95 | 1.05
70 | AVV_400_SK.K | 400 KV STATION AVEDØREVÆRKET | ENDKE | 400 | 0.95 | 1.05
71 | BAG_132_F | 132 KV STATION BAGSVÆRDGÅRD | ENDKE | 132 | 0.95 | 1.05
72 | BAL_132_F | 132 KV STATION BALLERUPGÅRD | ENDKE | 132 | 0.95 | 1.05
73 | BEL_132_A | 132 KV STATION BELLAHØJ KBST | ENDKE | 132 | 0.95 | 1.05
74 | BJS_016 | Bjæverskov | ENDKE | 15.8 | 0 | 1.05
75 | BJS_132_SFIK | 132 KV STATION BJÆVERSKOV | ENDKE | 132 | 0.95 | 1.05
76 | A2 | Bjæverskov | ENDKE | 232 | 0 | 1.05
77 | BJS_220_SFIK | Bjæverskov | ENDKE | 232 | 0 | 1.05
78 | BJS_400_K | 400 KV STATION BJÆVERSKOV | ENDKE | 400 | 0.95 | 1.05
82 | BLA_132_F | 132 KV STATION BLANGSLEV | ENDKE | 132 | 0.95 | 1.05
83 | BOR_132_F | 132 KV STATION BORUP | ENDKE | 132 | 0.95 | 1.05
84 | BRY_132_F | 132 KV STATION BRØNDBYGÅRD | ENDKE | 132 | 0.95 | 1.05
85 | DDS_1321_SFIK | 132 KV STATION STÅLVALSEVÆRKET | ENDKE | 132 | 0.95 | 1.05
86 | DDS_1322_SFIK | 132 KV STATION STÅLVALSEVÆRKET | ENDKE | 132 | 0.95 | 1.05
87 | DYR_132_F | 132 KV STATION DYREGÅRD | ENDKE | 132 | 0.95 | 1.05
88 | EBY_132_F | Ejbygård | ENDKE | 132 | 0.95 | 1.05
89 | ESK_132_F | 132 KV STATION ESKILSTRUP | ENDKE | 132 | 0.95 | 1.05
90 | FEM_132_F | 132 KV STATION FEMERN | ENDKE | 132 | 0 | 1.05
91 | FLA_132_WA2 | Flaskegård | ENDKE | 132 | 0.95 | 1.05
92 | FNM_132_F1 | Fensmark | ENDKE | 132 | 0.95 | 1.05
93 | GLN_010D_SFIK1 | Glentegård | ENDKE | 10 | 0.95 | 1.05
94 | GLN_010D_SFIK2 | Glentegård | ENDKE | 10 | 0 | 1.05
95 | GLN_132_F | Glentegård | ENDKE | 132 | 0.95 | 1.05
96 | GLN_400_SK.L | Glentegård | ENDKE | 400 | 0.95 | 1.05
97 | GRN_132_F1 | Grønnegård | ENDKE | 132 | 0.91 | 1.1
98 | GØR_132_F | 132 KV STATION GØRLØSE | ENDKE | 132 | 0.95 | 1.1
99 | GØR_132_SFIK | 132 KV STATION GØRLØSE | ENDKE | 132 | 0.95 | 1.1
100 | GØR_400_SKM2 | 400 KV STATION GØRLØSE | ENDKE | 400 | 0.95 | 1.05
101 | HASØ132_F | Haslev | ENDKE | 132 | 0.95 | 1.05
102 | HCV_132_A | H.C. Ørsted Værket | ENDKE | 132 | 0.95 | 1.05
103 | HCV_400_SK.A | H.C. Ørsted Værket | ENDKE | 400 | 0.95 | 1.05
104 | HDE_132_G | Hedegård | ENDKE | 132 | 0 | 1.05
105 | HEJ_132_F | 132 KV STATION HEJNINGE | ENDKE | 132 | 0.95 | 1.05
106 | HKS_010_S1 | Herslev | ENDKE | 10 | 0 | 1.05
107 | HKS_016 | Herslev | ENDKE | 15.8 | 0 | 1.05
108 | HKS_400_S1 | 400 KV KOBLINGSSTATION HERSLEV | ENDKE | 400 | 0.95 | 1.05
113 | HMA_132_F1 | Herlufmagle | ENDKE | 132 | 0.95 | 1.05
114 | HSKØ132_F | Hareskovgård | ENDKE | 132 | 0.95 | 1.05
115 | HSTØ132_F | Herstedgård | ENDKE | 132 | 0 | 1.05
116 | HVE_132_F | 132 KV STATION HOVEGÅRD | ENDKE | 132 | 0.98 | 1.05
117 | HVE_400_ | 400 KV STATION HOVEGÅRD | ENDKE | 400 | 1.02 | 1.04
118 | IDE_132_F | Idestrup | ENDKE | 132 | 0.95 | 1.05
119 | ISHN132_N-$ | 132 KV STATION ISHØJ | ENDKE | 132 | 0 | 1.05
120 | ISH_132_F | 132 KV STATION ISHØJ | ENDKE | 132 | 0.95 | 1.05
121 | ISH_220_S1 | 220 KV STATION ISHØJ | ENDKE | 232 | 0 | 1.05
122 | ISH_400_SK.K | 400 KV STATION ISHØJ | ENDKE | 400 | 0.95 | 1.05
123 | JER_132_F | Jersie | ENDKE | 132 | 0.95 | 1.05
124 | KAK_132_A | Kastrup Koblingstation | ENDKE | 132 | 0.95 | 1.05
125 | KAM_132_F | Kamstrup | ENDKE | 132 | 0.95 | 1.05
126 | KARA132_F | KARA Novoren Roskilde | ENDKE | 132 | 0 | 1.05
127 | KBG_132_SFIK1 | Kalundborg | ENDKE | 132 | 0.95 | 1.05
128 | KBG_132_SFIK2 | Kalundborg | ENDKE | 132 | 0.95 | 1.05
129 | KFA_220_S1 | Kriegers Flak A | ENDKE | 232 | 0 | 1.05
130 | KFB_220_S1 | Kriegers Flak B | ENDKE | 232 | 0 | 1.05
131 | KFE_000_S1 | Kriegers Flak C | ENDKE | 0.4 | 0 | 1.05
132 | KFE_010_S1 | Kriegers Flak C | ENDKE | 10 | 0 | 1.05
133 | KFE_150_S1 | Kriegers Flak C | ENDKE | 150 | 0 | 1.05
134 | KFE_220_S1 | Kriegers Flak C | ENDKE | 232 | 0 | 1.05
135 | KRL_132-WA1 | Karlstrup | ENDKE | 132 | 0 | 1.05
136 | KSV_132_F | Kirkeskovgård | ENDKE | 132 | 0.95 | 1.05
137 | KYV_0102_SFIK | KYNDBYVÆRKET B51 | ENDKE | 11 | 0.95 | 1.05
139 | KYV_0103_SFIK | KYNDBYVÆRKET B52 | ENDKE | 11 | 0.95 | 1.05
141 | KYV_0181_SFIK | KYNDBYVÆRKET B21 | ENDKE | 18 | 0.95 | 1.05
143 | KYV_0182_SFIK | KYNDBYVÆRKET B22 | ENDKE | 18 | 0.95 | 1.05
145 | KYV_132_SK.F | 132 KV STATION KYNDBYVÆRKET | ENDKE | 132 | 0.95 | 1.05
146 | EBY | Lindevang | ENDKE | 132 | 0.95 | 1.05
147 | LIN_132_F | Lindevang | ENDKE | 132 | 0.95 | 1.05
148 | LUP_132_F | Lyngerup | ENDKE | 132 | 0.95 | 1.05
149 | MAV_132_F | Masnedøværket | ENDKE | 132 | 0.95 | 1.05
150 | MOSØ132_WA2 | Mosedegård | ENDKE | 132 | 0.95 | 1.05
151 | MÅLØ132_F | Måløvgård | ENDKE | 132 | 0.95 | 1.05
152 | NAM_132_F | Nr. Asmindrup | ENDKE | 132 | 0.95 | 1.05
153 | NSV_132_F | Næstved | ENDKE | 132 | 0.95 | 1.05
154 | NVS_132_SFIK | Novo Syd | ENDKE | 132 | 0.95 | 1.05
155 | NYM_132_SFIK1 | Nymøllegård | ENDKE | 132 | 0.95 | 1.05
156 | NYM_132_SFIK2 | Nymøllegård | ENDKE | 132 | 0.95 | 1.05
157 | NYR_132_F | Nyrup | ENDKE | 132 | 0.95 | 1.05
158 | ORH_132_F1 | Orehoved | ENDKE | 132 | 0.95 | 1.05
159 | OST_132_F | Ostedgård | ENDKE | 132 | 0.95 | 1.05
160 | RAD_009_SFIK | Radsted | ENDKE | 9 | 1.02 | 1.03
161 | RAD_132_F | Radsted | ENDKE | 132 | 0.98 | 1.05
162 | RBY_132_F | Rødby | ENDKE | 132 | 0.95 | 1.05
163 | RDB_132_SFIK | VINDMØLLEPARK RØDSAND 2 | ENDKE | 132 | 0.91 | 1.1
164 | RDS_132_SFIK | 132 KV VINDMØLLEPARK RØDSAND 1 | ENDKE | 132 | 0.91 | 1.1
165 | RIL_132_F | 132 KV STATION RISLEV | ENDKE | 132 | 0.95 | 1.05
166 | RIN_132_F | Ringsted | ENDKE | 132 | 0.95 | 1.05
167 | SIB_132_F | Skibbygård | ENDKE | 132 | 0.95 | 1.1
168 | SKLØ132_F | Skuderløse | ENDKE | 132 | 0 | 1.05
169 | SMK_132_A | 132 KV SVANEMØLLE KBST | ENDKE | 132 | 0.95 | 1.05
170 | SOS_132_F | 132 KV STATION SØSTREMOSE | ENDKE | 132 | 0.95 | 1.05
171 | SPA_132_F | Spanager | ENDKE | 132 | 0.95 | 1.05
172 | SPR_132_F | Sperrestrupgård | ENDKE | 132 | 0.95 | 1.05
173 | STA_132_F | Stasevang | ENDKE | 132 | 0.95 | 1.05
174 | STSØ132_F1 | Statoil Syd | ENDKE | 132 | 0.95 | 1.1
175 | STV_0182_SFIK | Stigsnæsværket B2 | ENDKE | 18 | 0.95 | 1.05
176 | STV_132_F | Stigsnæsværket | ENDKE | 132 | 0.95 | 1.05
177 | MRP1 | Teglstrupgård | ENDKE | 132 | 0 | 1.05
178 | TOL_220_S1 | Tolstrup Gårde | ENDKE | 232 | 0.95 | 1.04
179 | TOR_132_F | Torslunde | ENDKE | 132 | 0.95 | 1.05
180 | VAL_132_WA2 | Valseværket | ENDKE | 132 | 0.95 | 1.05
181 | VSAK132_S1 | Valseværket | ENDKE | 132 | 0 | 1.05
182 | VEJ_132_F | Vejleå | ENDKE | 132 | 0.95 | 1.05
183 | VIK_132_A | Vigerslev | ENDKE | 132 | 0.95 | 1.05
184 | VIN_132_F | 132 KV STATION VINDINGEGÅRD | ENDKE | 132 | 0.95 | 1.05
185 | VLO_132_F | Vestlolland | ENDKE | 132 | 0.95 | 1.05
186 | VSA_132_S1 | Valseværket smelteri. Vorskla | ENDKE | 132 | 0 | 1.05
187 | ØLS_132_F | Ølstykkegård | ENDKE | 132 | 0.95 | 1.05
188 | ØSH_132_F | Østerholm | ENDKE | 132 | 0.95 | 1.05
189 | ØSV_132_F | Ørslevvester | ENDKE | 132 | 0 | 1.05
190 | ØSV_400_F | Ørslevvester | ENDKE | 400 | 0 | 1.05
191 | term_VL1_XBI_R11_K |  | dcVL | 400 | 0 | 1.05
192 | ABS_150_S2- | 150 KV STATION ABILDSKOV | ENDKW | 165 | 0 | 1.05
193 | I4 | 150 KV STATION ABILDSKOV | ENDKW | 165 | 0 | 1.05
194 | ADL_150_S1 | 150 KV STATION ÅDALEN | ENDKW | 165 | 0.88 | 1.03
195 | AHA_220_S1 | Anholt Havmøllepark | ENDKW | 232 | 0.98 | 1.02
196 | AND_150_S2 | 150 KV STATION ANDST | ENDKW | 165 | 0.88 | 1.03
197 | ASR_150_S2 | 150 kV STATION ASKÆR | ENDKW | 165 | 0.88 | 1.03
198 | ASR_400_S1 | 400 kV STATION ASKÆR | ENDKW | 400 | 0.9 | 1.05
199 | ASR_400-ZL- | 400 KV STATION Askær Reaktor skinne ZL | ENDKW | 400 | 0 | 1.05
200 | BBR_150_S1 | 150 KV STATION BREDEBRO | ENDKW | 165 | 0.97 | 1.01
201 | BDK_150_S1 | 150 KV STATION BREDKÆR | ENDKW | 165 | 0.88 | 1.03
202 | BDR_150_S1 | 150 KV STATION BRAMDRUP | ENDKW | 165 | 0.88 | 1.03
203 | BED_150_N | 150 KV STATION BEDSTED | ENDKW | 165 | 0.88 | 1.03
204 | BIL_150_S1 | 150 KV STATION BILSTRUP | ENDKW | 165 | 0 | 1.05
205 | BIX_150_S1 | 150 KV STATION BILSTRUP midlertidig | ENDKW | 165 | 0 | 1.05
206 | BJH_150_S1 | 150 KV STATION BJØRNHOLT | ENDKW | 165 | 0.97 | 1.01
207 | DYB_150_SA | 150 KV STATION DYBVAD | ENDKW | 165 | 0.88 | 1.03
208 | EDR_015_SFIK | 150 KV STATION ENDRUP | ENDKW | 15 | 1.02 | 1.03
209 | EDR_150_SV | 150 KV STATION ENDRUP | ENDKW | 165 | 0.88 | 1.03
210 | EDR_150_SØ2 | 150 KV STATION ENDRUP | ENDKW | 165 | 0.97 | 1.01
211 | EDR_220_S1 | Endrup | ENDKW | 232 | 0.97 | 1.03
212 | EDR_400_NIE1 | 400 KV STATION ENDRUP | ENDKW | 400 | 0 | 1.05
213 | EDR_400_NIE1(1) | 400 KV STATION ENDRUP | ENDKW | 400 | 0 | 1.05
214 | EDR_400_S1 | 400 KV STATION ENDRUP | ENDKW | 400 | 1.01 | 1.04
215 | EST_150_SFIK | 150 KV STATION ESTRUPVEJ | ENDKW | 165 | 0.88 | 1.03
216 | FER_150_S1 | 150 KV STATION FERSLEV | ENDKW | 165 | 0.97 | 1.01
217 | FER_400_S1 | 400 KV STATION FERSLEV | ENDKW | 400 | 1.01 | 1.04
218 | FGD_010_S1 | Fraugde | ENDKW | 10 | 0 | 1.05
219 | FGD_016 | Fraugde | ENDKW | 15.8 | 0 | 1.05
220 | FGD_150_S1 | 150 KV STATION FRAUGDE | ENDKW | 165 | 0.88 | 1.03
221 | FGD_400_S1 | 400 KV STATION FRAUGDE | ENDKW | 400 | 1.01 | 1.04
226 | FRD_150_S1 | 150 KV STATION FREDENSDAL | ENDKW | 165 | 0.88 | 1.03
227 | FRT_150_S1- | 150 KV STATION FRØSTRUP | ENDKW | 165 | 0.98 | 1.01
228 | FRX_150_S1 | 150 KV STATION Frøstrup midlertidig | ENDKW | 165 | 0 | 1.05
229 | FVO_010_SFIK | Fynsværket | ENDKW | 10.5 | 1.02 | 1.03
230 | FVO_021A_SFIK | Fynsværket | ENDKW | 21 | 1.02 | 1.03
231 | FVO_150_S1 | 150 KV STATION FYNSVÆRKET | ENDKW | 165 | 0.88 | 1.03
232 | FVO_400_SFIK | 400 KV STATION FYNSVÆRKET | ENDKW | 400 | 0.9 | 1.05
233 | GRP_150_S1 | 150 KV STATION GRADERUP | ENDKW | 165 | 0.88 | 1.03
234 | HASV150_SK1 | 150 KV STATION HASLE | ENDKW | 165 | 0.97 | 1.01
235 | HAT_150_SK1 | 150 KV STATION HATTING | ENDKW | 165 | 0.88 | 1.03
236 | HER_150_NORD | 150 KV STATION HERNING | ENDKW | 165 | 0.88 | 1.03
237 | VKHI012_SFIK | VESTKRAFT | ENDKW | 11.5 | 1.02 | 1.03
238 | HNB_150_S1 | 150 KV STATION HORNBÆK | ENDKW | 165 | 0.88 | 1.03
239 | HOD_150_SØ | 150 KV STATION HOLSTED | ENDKW | 165 | 0.88 | 1.03
240 | HRA_150_S1 | 150 kV HORNS REV HAVVIND A | ENDKW | 165 | 0.88 | 1.03
241 | HRB_150_S1 | 150 kV HORNS REV HAVVIND B | ENDKW | 165 | 0.98 | 1.02
242 | HRC_220_S1 | Horns Rev C | ENDKW | 232 | 0 | 1.05
243 | HSKV150_S1 | 150 KV STATION HØSKOV | ENDKW | 165 | 0.97 | 1.01
244 | HVO_150_S1 | 150 KV STATION HVORUPGAARD | ENDKW | 165 | 0.88 | 1.03
245 | HVV_150_S1 | 150 KV STATION HÅNDVÆRKERVEJ | ENDKW | 165 | 0 | 1.05
246 | HØN_150_S1 | 150 KV STATION HØRNING | ENDKW | 165 | 0.88 | 1.03
247 | IDU_150_N | 150 KV STATION IDUMLUND | ENDKW | 165 | 0.88 | 1.03
248 | IDU_400_S1 | 400 KV STATION IDUMLUND | ENDKW | 400 | 0.9 | 1.05
249 | KAE_150_N | 150 KV STATION KARLSGÅRDE | ENDKW | 165 | 0.88 | 1.03
250 | KAG_150_S1 | 150 kV KABELSTATION KATBJERG | ENDKW | 165 | 0.88 | 1.03
252 | KAS_150_SA | 150 KV STATION KASSØ | ENDKW | 165 | 0.88 | 1.03
253 | KAS_400_S1 | 400 KV STATION KASSØ | ENDKW | 400 | 0.9 | 1.05
254 | KBBV150_SFIK | 150 kV STATION KÆRBYBRO | ENDKW | 165 | 0.88 | 1.03
255 | KIN_150_S1 | 150 kV STATION KINGSTRUP | ENDKW | 165 | 0.88 | 1.03
256 | KIN_400_S1 | 400 kV STATION KINGSTRUP | ENDKW | 400 | 0.9 | 1.05
257 | KLF_150_S1 | 150 KV STATION KLIM FJORDHOLME | ENDKW | 165 | 0.88 | 1.03
258 | KLT_150_S1 | 150 kv T-AFGRENING KLIM FJORDHOLME | ENDKW | 165 | 0.88 | 1.03
259 | KNA_150_S1 | 150 KV STATION KNABBERUP | ENDKW | 165 | 0.88 | 1.03
260 | LAG_150_S1 | 150 KV STATION LANDERUPGAARD | ENDKW | 165 | 0.97 | 1.01
261 | LAG_400_S1 | 400 KV STATION LANDERUPGAARD | ENDKW | 400 | 0.9 | 1.05
262 | LGB_150_S1 | Lyngby | ENDKW | 165 | 0 | 1.05
263 | LKR_150_S2 | Lemkær | ENDKW | 165 | 0.97 | 1.01
264 | LOL_150_S1- | 150 KV STATION LOLDRUP | ENDKW | 165 | 0.97 | 1.01
265 | LYK_150_NORD | 150 KV STATION LYKKEGÅRD OG VKE | ENDKW | 165 | 0.88 | 1.03
266 | MAG_150_NORD | 150 KV STATION MAGSTRUP | ENDKW | 165 | 0.88 | 1.03
267 | MAL_150_S1 | 150 KV STATION MALLING | ENDKW | 165 | 0.88 | 1.03
268 | MAL_400_S1 | 400 KV STATION MALLING | ENDKW | 400 | 0.9 | 1.05
269 | MES_150_SK1 | 150 KV STATION MESBALLE | ENDKW | 165 | 0.88 | 1.03
270 | MKS_019A_SFIK | Studstrupværket | ENDKW | 19 | 1.02 | 1.03
271 | MKS_019B_SFIK | Studstrupværket | ENDKW | 19 | 1.02 | 1.03
272 | MKS_150_S1 | 150 KV STATION STUDSTRUP | ENDKW | 165 | 0.88 | 1.03
273 | MKS_400_SFIK | 400 KV STATION STUDSTRUP | ENDKW | 400 | 0.9 | 1.05
274 | MLP_150_S1 | 150 KV STATION MOLLERUP | ENDKW | 165 | 0.88 | 1.03
275 | MLU_150_S1 | 150 KV STATION MOSELUND | ENDKW | 165 | 0.88 | 1.03
276 | MOSV150_S1 | 150 KV STATION MOSBÆK | ENDKW | 165 | 0.88 | 1.03
277 | NOR_150_S1 | 150 KV STATION NORS | ENDKW | 165 | 0.88 | 1.03
278 | NSP_150_SA | 150 KV STATION NIBSTRUP | ENDKW | 165 | 0.97 | 1.01
279 | NVV_021A_SFIK | Vendsysselværket | ENDKW | 21 | 1.02 | 1.03
280 | NVV_021B_SFIK | Vendsysselværket | ENDKW | 21 | 1.02 | 1.03
281 | NVV_150_S1 | 150 KV STATION VENDSYSSELVÆRKET | ENDKW | 165 | 0.88 | 1.03
282 | NVV_400_S1 | 400 KV STATION VENDSYSSELVÆRKET | ENDKW | 400 | 0.9 | 1.05
283 | OSØ_150_S1 | 150 KV STATION ODENSE SYDØST | ENDKW | 165 | 0.88 | 1.03
284 | OVE_150_S1 | Odense Vest | ENDKW | 165 | 0 | 1.05
285 | RAM_150_S1 | 150 kV STATION RAMME | ENDKW | 165 | 0.88 | 1.03
286 | REV_400_S1- | 400 KV STATION REVSING | ENDKW | 400 | 0 | 1.05
287 | RIB_150_S1 | 150 KV STATION RIBE | ENDKW | 165 | 0.88 | 1.03
288 | RSL_150_S1 | Roslev | ENDKW | 165 | 0.97 | 1.01
289 | RYT_150_S1 | 150 KV STATION RYTTERGÅRD | ENDKW | 165 | 0.88 | 1.03
290 | SBA_150_S1 | 150 KV STATION STARBAKKE | ENDKW | 165 | 0.88 | 1.03
291 | SFE_150_SEK1 | 150 KV STATION SDR FELDING | ENDKW | 165 | 0.88 | 1.03
292 | SHE_021_SFIK | Enstedværket | ENDKW | 21 | 1.02 | 1.03
294 | SHE_150_SV1 | 150 KV STATION ENSTEDVÆRKET | ENDKW | 165 | 0.88 | 1.03
295 | SIN_150_S1 | Sindbjerg | ENDKW | 165 | 0.97 | 1.01
296 | SKA_150_SFIK | 150 KV STATION SKANSEN | ENDKW | 165 | 0.88 | 1.03
297 | STR_150_SV | 150 KV STATION STRUER | ENDKW | 165 | 0.88 | 1.03
298 | STSV150_N | 150 KV STATION STOVSTRUP | ENDKW | 165 | 0.88 | 1.03
299 | SVB_150_S1 | 150 KV STATION SVENDBORG | ENDKW | 165 | 0.88 | 1.03
300 | SVS_021_SFIK | Skærbækværket | ENDKW | 21 | 1.02 | 1.03
302 | SVS_150_S1 | 150 KV STATION SKÆRBÆKVÆRKET | ENDKW | 165 | 0.88 | 1.03
303 | SVS_400_SFIK | 400 KV STATION SKÆRBÆKVÆRKET | ENDKW | 400 | 0.9 | 1.05
304 | SØN_150_VEST | 150 KV STATION SØNDERBORG | ENDKW | 165 | 0.88 | 1.03
305 | TAN_150_SK1 | 150 KV STATION TANGE | ENDKW | 165 | 0.88 | 1.03
306 | THY_150_S1 | 150 KV STATION THYREGOD | ENDKW | 165 | 0.88 | 1.03
307 | THØ_150_S1 | 150 KV STATION TINGHØJ | ENDKW | 165 | 0.88 | 1.03
308 | TJE_010_S3 | Tjele | ENDKW | 10 | 0 | 1.05
309 | term_KT51-HT3 | Tjele | ENDKW | 10 | 0 | 1.05
310 | TJE_013_SFIK | Synkrongenerator Tjele | ENDKW | 13 | 1.02 | 1.03
311 | TJE_150_S1 | 150 KV STATION TJELE | ENDKW | 165 | 0 | 1.05
312 | TJE_150_S11 | 150 KV STATION TJELE | ENDKW | 165 | 0.97 | 1.01
316 | TJE_400_S1 | 400 KV STATION TJELE | ENDKW | 400 | 1.01 | 1.04
321 | TRI_150_S1 | 150 KV STATION TRIGE | ENDKW | 165 | 0.97 | 1.01
322 | TRI_220_S1 | Trige | ENDKW | 232 | 0 | 1.05
323 | TRI_400_S1 | 400 KV STATION TRIGE | ENDKW | 400 | 0.9 | 1.05
324 | VHA_010_SFIK | Vester Hassing | ENDKW | 10 | 1.02 | 1.03
325 | VHA_012_SFIK | Synkrongenerator Vester Hassing | ENDKW | 12 | 1.02 | 1.03
326 | VHA_150_S1- | 150 KV STATION VESTER HASSING | ENDKW | 165 | 0 | 1.05
327 | VHA_400_S1 | 400 KV STATION VESTER HASSING | ENDKW | 400 | 1.01 | 1.04
335 | VID_150_N | 150 KV STATION VIDEBÆK | ENDKW | 165 | 0.88 | 1.03
336 | VIL_150_S1 | 150 KV STATION VILSTED | ENDKW | 165 | 0.88 | 1.03
337 | VKE_019_S1 | VESTKRAFT | ENDKW | 19 | 1.02 | 1.03
338 | VKE_150_S1 | 150 kV STATION VESTKRAFT | ENDKW | 165 | 0.88 | 1.03
339 | ÅBØ_150_S1 | 150 KV STATION ÅLBORG ØST | ENDKW | 165 | 0.88 | 1.03
340 | ÅSP_150_S1 | 150 KV STATION ÅSTRUP | ENDKW | 165 | 0.88 | 1.03

## Line
Line Data | Energinet.dk | 2020
Node 1 | Node 2 | Line name | Area Name | Line type | Nominal Current[kA] | Nominal Voltage[kV] | Power (kW) | R1[Ohm] | X1[Ohm] | G1[uS] | B1[uS] | Length[km]
35 | 0 | MRP_132_XMO_TE31 | SVERIGE | Overhead Line | 0.89 | 132 | 117480 | 0.63 | 8.39 | 0 | 919.62 | 10
1 | 36 | MRP_132_XMO_TE32 | SVERIGE | Overhead Line | 0.89 | 132 | 117480 | 0.58 | 0.66 | 0 | 718.84 | 10
3 | 39 | SÅN_400_XSA_GO11 | SVERIGE | Overhead Line | 1.2 | 400 | 480000 | 1.78 | 19.24 | 0 | 1167.25 | 71.31
2 | 40 | SÅN_XSA_HO11 | SVERIGE | Overhead Line | 1.2 | 400 | 480000 | 0.01 | 0.16 | 0 | 2.04 | 0.58
8 | 9 | AUD_NBL1 | TYSKLAND | Null Line | 10 | 400 | 4000000 | 0 | 0 | 0 | 0 | 1
4 | 5 | BWT_KFDE | TYSKLAND | Null Line | 10 | 400 | 4000000 | 0.01 | 0.01 | 0 | 0 | 1
37 | 214 | EDR_400_NIEB11 | TYSKLAND | Overhead Line | 4 | 400 | 1600000 | 1.46 | 24.16 | 0 | 376.81 | 88
38 | 214 | EDR_400_NIEB21 | TYSKLAND | Overhead Line | 4 | 400 | 1600000 | 1.46 | 24.16 | 0 | 376.81 | 88
6 | 32 | FLE400_XFL_KA12 | TYSKLAND | Overhead Line | 2.15 | 400 | 860000 | 0.03 | 0.3 | 0 | 3.8 | 1
6 | 31 | FLE_400_XFL_KA11 | TYSKLAND | Overhead Line | 2.15 | 400 | 860000 | 0.03 | 0.3 | 0 | 3.8 | 1
6 | 9 | JARD2_UCTE | TYSKLAND | Null Line | 10 | 400 | 4000000 | 0.01 | 0.01 | 0 | 0 | 1
7 | 33 | JARD400_XJA_KA11 | TYSKLAND | Overhead Line | 2.15 | 400 | 860000 | 0.03 | 0.3 | 0 | 3.8 | 1
7 | 34 | JARD400_XJA_KA12 | TYSKLAND | Overhead Line | 2.15 | 400 | 860000 | 0.03 | 0.3 | 0 | 3.8 | 1
4 | 26 | KFE_400_XDE_DS12 | TYSKLAND | Cable | 1 | 150 | 150000 | 0.47 | 1.33 | 0 | 848.23 | 12
4 | 25 | KFE_400_XDE_DS21 | TYSKLAND | Cable | 1 | 150 | 150000 | 0.47 | 1.33 | 0 | 848.23 | 12
37 | 8 | NBL_400_XNI_BR11 | TYSKLAND | Overhead Line | 4 | 400 | 1600000 | 0.02 | 0.27 | 0 | 4.28 | 1
38 | 8 | NBL_400_XNI_BR12 | TYSKLAND | Overhead Line | 4 | 400 | 1600000 | 0.02 | 0.27 | 0 | 4.28 | 1
7 | 9 | UCTE_JARD1 | TYSKLAND | Null Line | 10 | 400 | 4000000 | 0.01 | 0.01 | 0 | 0 | 1
11 | 27 | z_EDR_400_XED_EE1D | dcCO | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
12 | 24 | BWT_400_XBW_BJ1K | dcKO | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
14 | 49 | z_XVH_LI11-LDO_132_KS2 | dcKS | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
51 | 13 | z_XVH_LI11-XVH_ST31_KS1 | dcKS | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
16 | 30 | z_HKS_400-XFG_HK12_SB1 | dcSB | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
15 | 29 | z_XFG_400-XFG_HK11_SB1 | dcSB | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
17 | 41 | z_XKR_TJ31-KSD_300_SK1 | dcSK | Equivalent Impedance | 9999 | 165 | 1649835000 | 0 | 0.27 | 0 | 0 | 0
18 | 43 | z_XTJE_150-SK2_XTJ_SK2 | dcSK | Equivalent Impedance | 9999 | 165 | 1649835000 | 0 | 0.27 | 0 | 0 | 0
19 | 45 | z_XTJE_400-SK3_XTJ_SK3 | dcSK | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
20 | 47 | z_XTJE_400_SK4_XKR_300_SK4 | dcSK | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 1.6 | 0 | 0 | 0
24 | 78 | BJS_400_XBW_BJ1K | ENDKE | Overhead Line | 0.88 | 400 | 352000 | 0 | 0 | 0 | 0 | 1
100 | 39 | GØR_400_XSA_GO11 | ENDKE | Overhead Line | 1.2 | 400 | 480000 | 1.1 | 11.84 | 0 | 718.42 | 43.89
40 | 117 | HVE_400_XSA_HO11 | ENDKE | Overhead Line | 1.2 | 400 | 480000 | 1.56 | 18.4 | 0 | 229.96 | 65.41
25 | 133 | KFE_400_XDE_DS11 | ENDKE | Cable | 1 | 150 | 150000 | 0.47 | 1.33 | 0 | 848.23 | 12
26 | 133 | KFE_400_XDE_DS12 | ENDKE | Cable | 1 | 150 | 150000 | 0.47 | 1.33 | 0 | 848.23 | 12
35 | 177 | TEG_132_XMO_TE31 | ENDKE | Overhead Line | 0.89 | 132 | 117480 | 0.63 | 8.39 | 0 | 919.62 | 10
36 | 177 | TGE_132_XMO_TE32 | ENDKE | Overhead Line | 0.89 | 132 | 117480 | 0.58 | 0.66 | 0 | 718.84 | 10
108 | 30 | XFG_HK12_HKS | ENDKE | Overhead Line | 1.2 | 400 | 480000 | 0 | 0.01 | 0 | 0 | 99.99
53 | 173 | eqZpu-43-114 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 8.75 | 68.64 | 0 | 0 | 0
83 | 173 | eqZpu-79-114 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 60.53 | 158.3 | 0 | 0 | 0
88 | 147 | eqZpu-18-33 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 2.66 | 21.48 | 0 | 0 | 0
89 | 161 | eqZpu-19-144 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 14.41 | 116.46 | 0 | 0 | 0
89 | 118 | eqZpu-19-89 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 14.61 | 141.63 | 0 | 0 | 0
118 | 161 | eqZpu-89-144 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 29.42 | 135.99 | 0 | 0 | 0
123 | 171 | eqZpu-102-108 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 10.8 | 127.71 | 0 | 0 | 0
127 | 128 | eqZpu-11-12 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 4.19 | 87.01 | 0 | 0 | 0
127 | 154 | eqZpu-11-137 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 0.4 | 73.24 | 0 | 0 | 0
128 | 154 | eqZpu-12-137 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 0.06 | 91.23 | 0 | 0 | 0
166 | 171 | eqZpu-106-108 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 30.81 | 164.77 | 0 | 0 | 0
168 | 101 | eqZpu-97-101 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 0.88 | 104.79 | 0 | 0 | 0
177 | 173 | eqZpu-26-114 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 13.16 | 63.11 | 0 | 0 | 0
177 | 180 | eqZpu-26-118 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 32.26 | 144.36 | 0 | 0 | 0
177 | 53 | eqZpu-26-43 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 29.52 | 118.26 | 0 | 0 | 0
177 | 83 | eqZpu-26-79 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 28.61 | 133.72 | 0 | 0 | 0
179 | 152 | eqZpu-27-34 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 4.35 | 105.91 | 0 | 0 | 0
180 | 181 | VAL_132_VSAK | ENDKE | Cable | 0.87 | 132 | 114840 | 0 | 0 | 0 | 1.96 | 0.03
182 | 84 | eqZpu-28-80 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 2.41 | 33 | 0 | 0 | 0
185 | 162 | eqZpu-37-105 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 29.26 | 97.34 | 0 | 0 | 0
185 | 161 | eqZpu-37-144 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 42.95 | 160.2 | 0 | 0 | 0
187 | 83 | eqZpu-38-79 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 20.95 | 92.64 | 0 | 0 | 0
188 | 153 | eqZpu-39-136 | ENDKE | Equivalent Impedance | 9999 | 132 | 1319868000 | 4.32 | 57.99 | 0 | 0 | 0
53 | 98 | ALL_132_GØR_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.55 | 3.73 | 0 | 79.3 | 10.14
53 | 173 | ALL_132_STA_eq_ElmLne | ENDKE | Cable | 1.23 | 132 | 162360 | 0.5 | 3.41 | 0 | 26.54 | 8.96
54 | 58 | AMF_132_AMV | ENDKE | Cable | 0.66 | 132 | 87120 | 0.01 | 0.03 | 0 | 21.68 | 0.3
55 | 58 | AMK_132_AMV1_eq_ElmLne | ENDKE | Cable | 0.46 | 132 | 60720 | 0.59 | 0.79 | 0 | 585.59 | 6.75
55 | 58 | AMK_132_AMV2_eq_ElmLne | ENDKE | Cable | 0.46 | 132 | 60720 | 0.61 | 0.82 | 0 | 573.66 | 6.89
55 | 102 | AMK_132_HCV1_eq_ElmLne | ENDKE | Cable | 0.52 | 132 | 68640 | 0.35 | 0.56 | 0 | 485.06 | 5
55 | 102 | AMK_132_HCV2_eq_ElmLne | ENDKE | Cable | 0.43 | 132 | 56760 | 0.54 | 0.76 | 0 | 569.57 | 6.7
55 | 124 | AMK_132_KAK_eq_ElmLne | ENDKE | Cable | 0.47 | 132 | 62040 | 0.41 | 0.55 | 0 | 351.67 | 4.36
58 | 73 | AMV_132_BEL_eq_ElmLne | ENDKE | Cable | 0.77 | 132 | 101640 | 0.24 | 1.76 | 0 | 756.81 | 9.64
58 | 95 | AMV_132_GLN_eq_ElmLne | ENDKE | Cable | 1 | 132 | 132000 | 0.33 | 3.15 | 0 | 2220.03 | 14.51
58 | 102 | AMV_132_HCV_eq_ElmLne | ENDKE | Cable | 0.62 | 132 | 81840 | 0.41 | 0.77 | 0 | 554.18 | 7.06
58 | 124 | AMV_132_KAK_eq_ElmLne | ENDKE | Cable | 0.44 | 132 | 58080 | 0.62 | 0.84 | 0 | 542.55 | 6.94
58 | 169 | AMV_132_SMK1_eq_ElmLne | ENDKE | Cable | 0.43 | 132 | 56760 | 0.58 | 1.79 | 0 | 573.13 | 6.8
58 | 169 | AMV_132_SMK2_eq_ElmLne | ENDKE | Cable | 0.43 | 132 | 56760 | 0.57 | 1.75 | 0 | 540.18 | 6.22
61 | 127 | ASV_132_KBG1_eq_ElmLne | ENDKE | Cable | 0.55 | 132 | 72600 | 0.29 | 0.45 | 0 | 139.92 | 3.18
61 | 128 | ASV_132_KBG2_eq_ElmLne | ENDKE | Cable | 0.4 | 132 | 52800 | 0.39 | 0.49 | 0 | 250.14 | 3.79
61 | 170 | ASV_132_SOS_eq_ElmLne | ENDKE | Cable | 1.12 | 132 | 147840 | 0.07 | 0.63 | 0 | 373.85 | 3.5
61 | 174 | ASV_132_STSØ_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.03 | 0.19 | 0 | 160.8 | 1.34
61 | 179 | ASV_132_TOR_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.56 | 10.57 | 0 | 241.37 | 28.55
63 | 108 | ASV_400_HKS_eq_ElmLne | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.48 | 6.81 | 0 | 79.94 | 22
63 | 190 | ASV_400_ØSV | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.83 | 11.85 | 0 | 139.09 | 38.28
68 | 84 | AVV_132_BRY1_eq_ElmLne | ENDKE | Cable | 0.61 | 132 | 80520 | 0.34 | 0.9 | 0 | 412.02 | 6.54
68 | 84 | AVV_132_BRY2_eq_ElmLne | ENDKE | Cable | 0.61 | 132 | 80520 | 0.34 | 0.9 | 0 | 411.39 | 6.53
68 | 84 | AVV_132_BRY3_eq_ElmLne | ENDKE | Cable | 0.61 | 132 | 80520 | 0.34 | 0.91 | 0 | 417.69 | 6.63
70 | 103 | AVV_400_HCV__eq_ElmLne | ENDKE | Cable | 1.15 | 400 | 460000 | 0.15 | 1.74 | 0 | -65.78 | 8.9
70 | 122 | AVV_400_ISH_eq_ElmLne | ENDKE | Cable | 1.41 | 400 | 564000 | 0.2 | 2.38 | 0 | 132.1 | 12.05
71 | 97 | BAG_132_GRN_eq_ElmLne | ENDKE | Cable | 0.69 | 132 | 91080 | 0.14 | 0.31 | 0 | 196.56 | 2.73
71 | 114 | BAG_132_HSK1_eq_ElmLne | ENDKE | Cable | 0.58 | 132 | 76560 | 0.33 | 0.47 | 0 | 182.59 | 3.63
71 | 114 | BAG_132_HSK2_eq_ElmLne | ENDKE | Cable | 0.54 | 132 | 71280 | 0.49 | 0.58 | 0 | 201.7 | 4.26
72 | 87 | BAL_132_DYR_eq_ElmLne | ENDKE | Cable | 0.77 | 132 | 101640 | 0.17 | 0.24 | 0 | 138.6 | 2.1
72 | 116 | BAL_132_HVE_eq_ElmLne | ENDKE | Cable | 0.77 | 132 | 101640 | 0.45 | 3.69 | 0 | 659.34 | 9.99
73 | 95 | BEL_132_GLN1(1)_eq_ElmLne | ENDKE | Cable | 0.91 | 132 | 120120 | 0.49 | 2.72 | 0 | 792.04 | 6.8
73 | 147 | BEL_132_LIN_eq_ElmLne | ENDKE | Cable | 0.51 | 132 | 67320 | 0.23 | 0.37 | 0 | 334.58 | 3.45
73 | 169 | BEL_132_SMK_eq_ElmLne | ENDKE | Cable | 0.46 | 132 | 60720 | 0.46 | 0.63 | 0 | 328.92 | 5.2
75 | 171 | BJS_132_SPA(1)_eq_ElmLne | ENDKE | Cable | 1.84 | 132 | 242880 | 0.05 | 0.35 | 0 | 618.58 | 4
77 | 178 | BJS_220_TOL | ENDKE | Cable | 1.1 | 232 | 255200 | 0.13 | 1.65 | 0 | 650.56 | 8.27
78 | 117 | BJS_400_HVE_eq_ElmLne | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.81 | 11.55 | 0 | 135.53 | 37.3
78 | 122 | BJS_400_ISH_eq_ElmLne | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.7 | 9.96 | 0 | 116.89 | 32.17
78 | 190 | BJS_400_ØSV | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.65 | 9.29 | 0 | 109.01 | 30
82 | 92 | BLA_132_FNM_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.74 | 5.02 | 0 | 39.26 | 13.27
82 | 149 | BLA_132_MAV_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.11 | 7.95 | 0 | 236.87 | 21.22
82 | 158 | BLA_132_ORH_eq_ElmLne | ENDKE | Cable | 0.79 | 132 | 104280 | 1.49 | 9.08 | 0 | 676.83 | 27.02
82 | 165 | BLA_132_RIL_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.03 | 6.99 | 0 | 54.54 | 18.43
83 | 98 | BOR_132_GØR1_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.11 | 0.75 | 0 | 76.09 | 2.46
83 | 98 | BOR_132_GØR2_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.11 | 0.74 | 0 | 69.93 | 2.39
83 | 116 | BOR_132_HVE_eq_ElmLne | ENDKE | Cable | 1.23 | 132 | 162360 | 1.21 | 8.26 | 0 | 64.29 | 21.7
83 | 172 | BOR_132_SPR_eq_ElmLne | ENDKE | Cable | 1.23 | 132 | 162360 | 0.78 | 5.27 | 0 | 41.06 | 13.86
83 | 180 | BOR_132_VAL1 | ENDKE | Cable | 0.91 | 132 | 120120 | 0.41 | 2.58 | 0 | 1211.71 | 13.3
83 | 180 | BOR_132_VAL2 | ENDKE | Cable | 0.91 | 132 | 120120 | 0.41 | 2.58 | 0 | 1211.71 | 13.3
84 | 88 | BRY_132_EBY | ENDKE | Cable | 0.96 | 132 | 126720 | 0.18 | 0.77 | 0 | 833.15 | 7.8
84 | 119 | BRY_132_ISH | ENDKE | Cable | 0.96 | 132 | 126720 | 0.16 | 0.68 | 0 | 737.02 | 6.9
85 | 180 | DDS_132_VAL1_eq_ElmLne | ENDKE | Cable | 0.69 | 132 | 91080 | 0.02 | 0.04 | 0 | 17.91 | 0.3
86 | 180 | DDS_132_VAL2_eq_ElmLne | ENDKE | Cable | 0.69 | 132 | 91080 | 0.02 | 0.04 | 0 | 17.91 | 0.3
87 | 88 | DYR_132_EBY_eq_ElmLne | ENDKE | Cable | 0.81 | 132 | 106920 | 0.37 | 0.93 | 0 | 485.1 | 7.35
87 | 114 | DYR_132_HSKØ_eq_ElmLne | ENDKE | Cable | 0.77 | 132 | 101640 | 0.18 | 0.3 | 0 | 170.94 | 2.59
88 | 97 | EBY_132_GRN_eq_ElmLne | ENDKE | Cable | 0.69 | 132 | 91080 | 0.5 | 1.14 | 0 | 714.96 | 9.93
88 | 115 | EBY_132_HST | ENDKE | Cable | 0.79 | 132 | 104280 | 0.12 | 0.4 | 0 | 346.2 | 3.8
88 | 146 | EBY_132_LIN_eq_ElmLne | ENDKE | Cable | 0.5 | 132 | 66000 | 0.49 | 0.92 | 0 | 768.24 | 7.92
89 | 118 | ESK_132_IDE_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.68 | 4.59 | 0 | 35.98 | 12.18
89 | 149 | ESK_132_MAV_eq_ElmLne | ENDKE | Cable | 0.79 | 132 | 104280 | 1.11 | 5.96 | 0 | 568.49 | 19.16
89 | 161 | ESK_132_RAD_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.84 | 5.57 | 0 | 211.98 | 16.37
90 | 162 | FEM_132_RBY | ENDKE | Cable | 0.91 | 132 | 120120 | 0.19 | 1.24 | 0 | 581.9 | 6.39
90 | 185 | FEM_132_VLO | ENDKE | Cable | 0.91 | 132 | 120120 | 0.74 | 4.73 | 0 | 2221.62 | 24.39
91 | 120 | FLA_132_ISH1_eq_ElmLne | ENDKE | Cable | 1.16 | 132 | 153120 | 0.06 | 0.61 | 0 | 281.49 | 2.8
91 | 120 | FLA_132_ISH2_eq_ElmLne | ENDKE | Cable | 1.16 | 132 | 153120 | 0.06 | 0.61 | 0 | 281.49 | 2.8
91 | 125 | FLA_132_KAM_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.84 | 5.74 | 0 | 44.68 | 15.09
91 | 150 | FLA_132_MOSØ_eq_ElmLne | ENDKE | Cable | 0.86 | 132 | 113520 | 0.16 | 1.37 | 0 | 528.42 | 5.8
91 | 159 | FLA_132_OST_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.18 | 8.02 | 0 | 62.25 | 21.06
92 | 165 | FNM_132_RIL_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.38 | 2.61 | 0 | 20.36 | 6.88
92 | 168 | FNM_132_SKL | ENDKE | Cable | 1.12 | 132 | 147840 | 0.14 | 1.24 | 0 | 737.02 | 6.9
95 | 169 | GLN_132_SMK_eq_ElmLne | ENDKE | Cable | 0.46 | 132 | 60720 | 1.14 | 6.01 | 0 | 1053.06 | 12.06
95 | 173 | GLN_132_STA_eq_ElmLne | ENDKE | Cable | 1.1 | 132 | 145200 | 0.36 | 3.45 | 0 | 2102.04 | 17.52
96 | 117 | GLN_400_HVE_eq_ElmLne | ENDKE | Cable | 1.16 | 400 | 464000 | 0.36 | 3.95 | 0 | 91.04 | 18.88
98 | 173 | GØR_132_STA_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.05 | 7.14 | 0 | 105.85 | 19.1
100 | 117 | GØR_400_HVE_eq_ElmLne | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.45 | 6.43 | 0 | 75.47 | 20.77
168 | 101 | HASØ132_SKL | ENDKE | Cable | 1.12 | 132 | 147840 | 0.13 | 1.11 | 0 | 662.25 | 6.2
101 | 171 | HASØ132_SPA_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.93 | 6.23 | 0 | 168.08 | 17.72
102 | 147 | HCV_132_LIN_eq_ElmLne | ENDKE | Cable | 0.55 | 132 | 72600 | 0.42 | 0.74 | 0 | 490.72 | 6.25
102 | 183 | HCV_132_VIK_eq_ElmLne | ENDKE | Cable | 0.51 | 132 | 67320 | 0.34 | 0.53 | 0 | 458.67 | 4.73
104 | 125 | HDE_132_KAM_eq_ElmLne | ENDKE | Cable | 0.9 | 132 | 118800 | 0.28 | 1.58 | 0 | 540.35 | 6.88
104 | 126 | HDE_132_KARA_eq_ElmLne | ENDKE | Cable | 0.66 | 132 | 87120 | 0.03 | 0.07 | 0 | 46.97 | 0.65
104 | 184 | HDE_132_VIN_eq_ElmLne | ENDKE | Cable | 0.9 | 132 | 118800 | 0.1 | 0.58 | 0 | 196.35 | 2.5
105 | 157 | HEJ_132_NYR_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.57 | 10.71 | 0 | 83.34 | 28.31
105 | 176 | HEJ_132_STV_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.44 | 9.78 | 0 | 76.53 | 25.9
108 | 117 | HKS_400_HVE | ENDKE | Cable | 1.08 | 400 | 432000 | 1.77 | 22.17 | 0 | 1010.73 | 86
113 | 153 | HMA_132_NSV | ENDKE | Cable | 1.12 | 132 | 147840 | 0.23 | 2 | 0 | 1196.32 | 11.2
113 | 166 | HMA_132_RIN_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.64 | 4.36 | 0 | 34.15 | 11.56
114 | 151 | HSKØ132_MÅL_eq_ElmLne | ENDKE | Cable | 0.77 | 132 | 101640 | 0.34 | 0.57 | 0 | 318.78 | 4.83
115 | 182 | HST_132_VEJ | ENDKE | Cable | 0.79 | 132 | 104280 | 0.15 | 0.97 | 0 | 455.53 | 5
116 | 145 | HVE_132_KYV1_eq_ElmLne | ENDKE | Cable | 1.99 | 132 | 262680 | 0.55 | 7.78 | 0 | 99.37 | 24.9
116 | 145 | HVE_132_KYV2_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.42 | 9.63 | 0 | 74.91 | 25.29
116 | 148 | HVE_132_LUP_eq_ElmLne | ENDKE | Cable | 1.99 | 132 | 262680 | 0.4 | 5.64 | 0 | 76.21 | 18.28
116 | 151 | HVE_132_MÅL_eq_ElmLne | ENDKE | Cable | 0.77 | 132 | 101640 | 0.34 | 2.85 | 0 | 68.92 | 7.75
116 | 182 | HVE_132_VEJ1_eq_ElmLne | ENDKE | Cable | 1.99 | 132 | 262680 | 0.28 | 3.66 | 0 | 32.13 | 10.21
116 | 182 | HVE_132_VEJ2_eq_ElmLne | ENDKE | Cable | 1.99 | 132 | 262680 | 0.28 | 3.66 | 0 | 32.13 | 10.21
117 | 122 | HVE_400_ISH_eq_ElmLne | ENDKE | Cable | 2.91 | 400 | 1164000 | 0.37 | 5.26 | 0 | 61.7 | 16.98
117 | 122 | HVE_400_ISH2 | ENDKE | Cable | 1.19 | 400 | 476000 | 0.38 | 3.51 | 0 | 744.99 | 17.45
119 | 182 | ISH_132_VEJ | ENDKE | Cable | 0.96 | 132 | 126720 | 0.09 | 0.39 | 0 | 416.58 | 3.9
120 | 184 | ISH_132_VIN | ENDKE | Cable | 0.91 | 132 | 120120 | 0.4 | 2.54 | 0 | 1193.49 | 13.1
121 | 178 | ISH_220_TOL | ENDKE | Cable | 1.1 | 232 | 255200 | 0.54 | 7.01 | 0 | 2761.16 | 35.1
123 | 135 | JER_132_KRL_eq_ElmLne | ENDKE | Cable | 1.04 | 132 | 137280 | 0.1 | 0.68 | 0 | 250 | 2.74
123 | 171 | JER_132_SPA(1)_eq_ElmLne | ENDKE | Cable | 1.24 | 132 | 163680 | 0.27 | 2.47 | 0 | 57.25 | 11.1
125 | 136 | KAM_132_KSV_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.74 | 5.03 | 0 | 39.05 | 13.19
125 | 171 | KAM_132_SPA_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.84 | 5.68 | 0 | 44.08 | 14.93
125 | 184 | KAM_132_VIN_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.42 | 2.84 | 0 | 22.03 | 7.44
129 | 130 | KFA_220_KFB | ENDKE | Cable | 1.06 | 232 | 245920 | 0.48 | 1.29 | 0 | 698.06 | 11
129 | 178 | KFA_220_TOL | ENDKE | Cable | 1.06 | 232 | 245920 | 2.31 | 10.29 | 0 | 2636.04 | 69.54
130 | 134 | KFB_220_KFE | ENDKE | Cable | 10 | 232 | 2320000 | 0 | 0 | 0 | 0 | 0.01
130 | 178 | KFB_220_TOL | ENDKE | Cable | 1.06 | 232 | 245920 | 2.36 | 10.4 | 0 | 2699.52 | 70.54
135 | 150 | KRL_132_MOSØ_eq_ElmLne | ENDKE | Cable | 0.86 | 132 | 113520 | 0.27 | 1.31 | 0 | 819.04 | 8.99
136 | 174 | KSV_132_STSØ_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 3.06 | 20.77 | 0 | 161.18 | 54.43
136 | 179 | KSV_132_TOR_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.57 | 10.66 | 0 | 82.64 | 27.91
136 | 182 | KSV_132_VEJ_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.97 | 13.36 | 0 | 103.61 | 34.99
145 | 148 | KYV_132_LUP_eq_ElmLne | ENDKE | Cable | 1.99 | 132 | 262680 | 0.16 | 2.25 | 0 | 24.1 | 6.92
145 | 187 | KYV_132_ØLS_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.98 | 6.7 | 0 | 52.11 | 17.59
147 | 183 | LIN_132_VIK_eq_ElmLne | ENDKE | Cable | 0.51 | 132 | 67320 | 0.26 | 0.42 | 0 | 368.51 | 3.75
148 | 167 | LUP_132_SIB_eq_ElmLne | ENDKE | Cable | 0.54 | 132 | 71280 | 0.83 | 1.05 | 0 | 440.01 | 8.24
152 | 179 | NAM_132_TOR_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.09 | 7.37 | 0 | 56.96 | 19.3
153 | 165 | NSV_132_RIL1_eq_ElmLne | ENDKE | Cable | 1.28 | 132 | 168960 | 0.22 | 1.49 | 0 | 11.61 | 3.92
153 | 165 | NSV_132_RIL2_eq_ElmLne | ENDKE | Cable | 1.28 | 132 | 168960 | 0.22 | 1.49 | 0 | 11.61 | 3.92
153 | 176 | NSV_132_STV1_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.71 | 11.6 | 0 | 90.65 | 30.68
153 | 176 | NSV_132_STV2_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.75 | 11.87 | 0 | 92.88 | 31.42
153 | 188 | NSV_132_ØSH_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.32 | 2.15 | 0 | 16.86 | 5.71
154 | 170 | NVS_132_SOS_eq_ElmLne | ENDKE | Cable | 0.55 | 132 | 72600 | 0.23 | 0.41 | 0 | 191.04 | 3.2
155 | 184 | NYM_132_VIN1_eq_ElmLne | ENDKE | Cable | 0.56 | 132 | 73920 | 0.07 | 0.12 | 0 | 33.46 | 0.82
156 | 184 | NYM_132_VIN2_eq_ElmLne | ENDKE | Cable | 0.5 | 132 | 66000 | 0.07 | 0.12 | 0 | 41.11 | 0.86
157 | 159 | NYR_132_OST_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.28 | 8.8 | 0 | 67.72 | 23.04
157 | 189 | NYR_132_ØSV | ENDKE | Cable | 1.12 | 132 | 147840 | 0.17 | 1.43 | 0 | 854.51 | 8
158 | 161 | ORH_132_RAD1(1)_eq_ElmLne | ENDKE | Cable | 0.82 | 132 | 108240 | 1.22 | 8.02 | 0 | 226.78 | 22.1
158 | 161 | ORH_132_RAD2_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.3 | 8.11 | 0 | 146.96 | 22.16
158 | 188 | ORH_132_ØSH | ENDKE | Cable | 0.79 | 132 | 104280 | 1.84 | 10.63 | 0 | 1173.18 | 34.55
161 | 162 | RAD_132_RBY_eq_ElmLne | ENDKE | Cable | 0.55 | 132 | 72600 | 1.93 | 3.21 | 0 | 1372.08 | 25.39
161 | 163 | RAD_132_RDB_eq_ElmLne | ENDKE | Cable | 0.94 | 132 | 124080 | 1.13 | 5.4 | 0 | 3115.01 | 36.9
161 | 164 | RAD_132_RDS_eq_ElmLne | ENDKE | Cable | 0.79 | 132 | 104280 | 1.04 | 3.21 | 0 | -250.77 | 28.7
165 | 171 | RIL_132_SPA1_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.93 | 13.12 | 0 | 102.12 | 34.47
165 | 171 | RIL_132_SPA2_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.93 | 13.12 | 0 | 102.12 | 34.47
166 | 189 | RIN_132_ØSV | ENDKE | Cable | 1.12 | 132 | 147840 | 0.17 | 1.43 | 0 | 854.51 | 8
172 | 187 | SPR_132_ØLS_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.63 | 4.25 | 0 | 33.12 | 11.18
173 | 177 | STA_132_TEG1_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 1.05 | 7.13 | 0 | 55.02 | 18.71
173 | 177 | STA_132_TEG2_eq_ElmLne | ENDKE | Cable | 0.75 | 132 | 99000 | 1.44 | 7.85 | 0 | 57.79 | 20.13
176 | 185 | STV_132_VLO__eq_ElmLne | ENDKE | Cable | 1.19 | 132 | 157080 | 1.39 | 2.67 | 0 | 3676.28 | 47.3
181 | 186 | VAL_132_VSA_eq_ElmLne | ENDKE | Cable | 0.55 | 132 | 72600 | 0.03 | 0.46 | 0 | 102.1 | 1.3
182 | 184 | VEJ_132_VIN_eq_ElmLne | ENDKE | Cable | 0.88 | 132 | 116160 | 0.84 | 5.72 | 0 | 44.31 | 14.96
22 | 286 | XBI_R11_K_REV_400 | dcVL | Overhead Line | 2.2 | 400 | 880000 | 0 | 0.01 | 0 | 0 | 1
191 | 22 | z_REV_400_XBI_R11_K | dcVL | Equivalent Impedance | 9999 | 400 | 3999600000 | 0 | 0 | 0 | 0 | 0
27 | 214 | EDR_400_XED_EE1D | ENDKW | Overhead Line | 2.21 | 400 | 884000 | 0.03 | 0.3 | 0 | 3.88 | 1
253 | 31 | KAS_400_XFL_KA11 | ENDKW | Overhead Line | 2.15 | 400 | 860000 | 0.52 | 5.94 | 0 | 76 | 20
253 | 32 | KAS_400_XFL_KA12 | ENDKW | Overhead Line | 2.15 | 400 | 860000 | 0.52 | 5.94 | 0 | 76 | 20
253 | 33 | KAS_400_XJA_KA11 | ENDKW | Overhead Line | 2.15 | 400 | 860000 | 0.52 | 5.94 | 0 | 76 | 20
253 | 34 | KAS_400_XJA_KA12 | ENDKW | Overhead Line | 2.15 | 400 | 860000 | 0.52 | 5.94 | 0 | 76 | 20
29 | 221 | XFG_HK11_HKS | ENDKW | Overhead Line | 1.2 | 400 | 480000 | 0 | 0.01 | 0 | 0 | 99.99
45 | 316 | XJR_TJ31_TJE | ENDKW | Overhead Line | 0.92 | 400 | 368000 | 0 | 0 | 0 | 0 | 1
47 | 316 | XJR_TJ41_TJE | ENDKW | Overhead Line | 0.92 | 400 | 368000 | 0 | 0 | 0 | 0 | 1
41 | 312 | XKR_TJ13_TJE | ENDKW | Overhead Line | 0.92 | 165 | 151800 | 0 | 0.05 | 0 | 0 | 36.8
43 | 312 | XKR_TJ21_TJE | ENDKW | Overhead Line | 0.92 | 165 | 151800 | 0 | 0 | 0 | 0 | 1
49 | 327 | XVH_LI11_VHA | ENDKW | Overhead Line | 0.88 | 400 | 352000 | 0 | 0.05 | 0 | 0 | 9.78
51 | 327 | XVH_LI21_VHA | ENDKW | Overhead Line | 0.88 | 400 | 352000 | 0 | 0.05 | 0 | 0 | 9.78
192 | 284 | ABS_150_OVE | ENDKW | Cable | 0.77 | 165 | 127050 | 1.25 | 8.64 | 0 | 273.62 | 23.19
192 | 299 | ABS_150_SVB_eq_ElmLne | ENDKW | Cable | 0.99 | 165 | 163350 | 2.02 | 14.46 | 0 | 101.75 | 36.2
193 | 304 | ABS_150_SØN_eq_ElmLne | ENDKW | Cable | 0.75 | 165 | 123750 | 1.52 | 9.7 | 0 | 2614.84 | 50
194 | 216 | ADL_150_FER_eq_ElmLne | ENDKW | Cable | 0.93 | 165 | 153450 | 0.19 | 1.61 | 0 | 775.41 | 8.6
194 | 245 | ADL_150_HVV_eq_ElmLne | ENDKW | Cable | 0.93 | 165 | 153450 | 0.04 | 0.3 | 0 | 162.3 | 1.8
194 | 339 | ADL_150_ÅBØ_eq_ElmLne | ENDKW | Cable | 1.1 | 165 | 181500 | 0.27 | 2.36 | 0 | 1259.08 | 13.82
195 | 322 | AHA_220_TRI__eq_ElmLne | ENDKW | Cable | 1.02 | 232 | 236640 | 2.09 | 15.9 | 0 | 3872.91 | 84.3
196 | 202 | AND_150_BDR_eq_ElmLne | ENDKW | Cable | 1.16 | 165 | 191400 | 1.1 | 7.41 | 0 | 40.71 | 16.39
196 | 239 | AND_150_HOD | ENDKW | Cable | 0.93 | 165 | 153450 | 0.76 | 15 | 0 | 2017.53 | 24.7
196 | 266 | AND_150_MAG_eq_ElmLne | ENDKW | Cable | 0.98 | 165 | 161700 | 1.73 | 9.89 | 0 | 65.22 | 24
197 | 236 | ASR_150_HER | ENDKW | Cable | 1.13 | 165 | 186450 | 0.68 | 5.82 | 0 | 3165.15 | 32.5
197 | 306 | ASR_150_THY_eq_ElmLne | ENDKW | Cable | 0.94 | 165 | 155100 | 0.14 | 1.12 | 0 | 448.8 | 5.1
198 | 286 | ASR_400_REV_eq_ElmLne | ENDKW | Cable | 2.4 | 400 | 960000 | 0.85 | 14 | 0 | 218.38 | 51
198 | 316 | ASR_400_TJE__eq_ElmLne | ENDKW | Cable | 2.15 | 400 | 860000 | 1.11 | 17.85 | 0 | 688.18 | 68.9
200 | 252 | BBR_150_KAS_eq_ElmLne | ENDKW | Cable | 1.13 | 165 | 186450 | 0.67 | 5.71 | 0 | 3106.72 | 31.9
200 | 265 | BBR_150_LYK_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 3.7 | 21.43 | 0 | 358.55 | 58.23
200 | 287 | BBR_150_RIB | ENDKW | Cable | 1.5 | 165 | 247500 | 1.93 | 11.49 | 0 | 91.9 | 30.7
201 | 278 | BDK_150_NSP_eq_ElmLne | ENDKW | Cable | 0.18 | 165 | 29700 | 1.01 | 4.98 | 0 | 1555.65 | 23.58
201 | 281 | BDK_150_NVV_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 3.68 | 11.99 | 0 | 1450.76 | 44.2
202 | 260 | BDR_150_LAG_eq_ElmLne | ENDKW | Cable | 1.13 | 165 | 186450 | 0.27 | 2.31 | 0 | 1259.24 | 12.93
203 | 277 | BED_150_NOR1_eq_ElmLne | ENDKW | Cable | 0.9 | 165 | 148500 | 1 | 6.38 | 0 | 521.84 | 32.9
203 | 295 | BED_150_SIN | ENDKW | Cable | 0.9 | 165 | 148500 | 0.7 | 4.4 | 0 | 1870.5 | 23.2
203 | 297 | BED_150_STR_eq_ElmLne | ENDKW | Cable | 0.9 | 165 | 148500 | 1.43 | 9.12 | 0 | 3839.03 | 47
204 | 205 | BIL_150_BIX_eq_ElmLne | ENDKW | Cable | 10 | 165 | 1650000 | 0 | 0 | 0 | 0 | 0.01
204 | 247 | BIL_150_IDU | ENDKW | Cable | 0.62 | 165 | 102300 | 1.22 | 7.76 | 0 | 3267.26 | 40
204 | 264 | BIL_150_LOL_eq_ElmLne | ENDKW | Cable | 1.01 | 165 | 166650 | 0.71 | 6.63 | 0 | 2368.52 | 29
288 | 204 | BIL_150_RSL | ENDKW | Cable | 0.9 | 165 | 148500 | 0.64 | 4.07 | 0 | 1715.31 | 21
206 | 236 | BJH_150_HER | ENDKW | Cable | 0.93 | 165 | 153450 | 1.35 | 11.84 | 0 | 1888.35 | 50.9
206 | 305 | BJH_150_TAN_eq_ElmLne | ENDKW | Cable | 0.93 | 165 | 153450 | 0.47 | 4.35 | 0 | 1658.13 | 20.3
207 | 290 | DYB_150_SBA_eq_ElmLne | ENDKW | Cable | 0.84 | 165 | 138600 | 1.8 | 9.7 | 0 | 71.19 | 24.9
207 | 326 | DYB_150_VHA_eq_ElmLne | ENDKW | Cable | 0.84 | 165 | 138600 | 2.63 | 14.34 | 0 | 102.75 | 36.4
209 | 239 | EDR_150_HOD_eq_ElmLne | ENDKW | Cable | 0.93 | 165 | 153450 | 0.45 | 2.89 | 0 | 1216.24 | 14.89
210 | 241 | EDR_150_HRB_eq_ElmLne | ENDKW | Cable | 0.78 | 165 | 128700 | 4.47 | 11.27 | 0 | 4188.73 | 98.24
209 | 265 | EDR_150_LYK1_eq_ElmLne | ENDKW | Cable | 0.98 | 165 | 161700 | 1.16 | 6.09 | 0 | 47.14 | 16
209 | 265 | EDR_150_LYK2_eq_ElmLne | ENDKW | Cable | 0.98 | 165 | 161700 | 1.16 | 6.09 | 0 | 47.14 | 16
211 | 242 | EDR_220_HRC | ENDKW | Cable | 1.02 | 232 | 236640 | 2.19 | 14.09 | 0 | 3459.4 | 79.8
214 | 286 | EDR_400_REV1 | ENDKW | Cable | 2.76 | 400 | 1104000 | 0.65 | 8.65 | 0 | 117.17 | 30.13
214 | 286 | EDR_400_REV2 | ENDKW | Cable | 2.76 | 400 | 1104000 | 0.65 | 8.65 | 0 | 117.17 | 30.13
215 | 265 | EST_150_LYK_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 0.36 | 1.17 | 0 | 8.58 | 3
216 | 276 | FER_150_MOSV_eq_ElmLne | ENDKW | Cable | 1.2 | 165 | 198000 | 1.05 | 8.74 | 0 | 78.46 | 24.74
216 | 307 | FER_150_THØ_eq_ElmLne | ENDKW | Cable | 0.75 | 165 | 123750 | 1.62 | 9.92 | 0 | 218.86 | 40.35
217 | 282 | FER_400_NVV__eq_ElmLne | ENDKW | Cable | 1.38 | 400 | 552000 | 0.42 | 4.61 | 0 | 84.72 | 20.4
217 | 316 | FER_400_TJE_eq_ElmLne | ENDKW | Cable | 1.6 | 400 | 640000 | 1.52 | 19.13 | 0 | 223.29 | 61.57
217 | 323 | FER_400_TRI__eq_ElmLne | ENDKW | Cable | 1.4 | 400 | 560000 | 2.03 | 25.41 | 0 | 581.92 | 92.1
217 | 327 | FER_400_VHA_eq_ElmLne | ENDKW | Cable | 1.22 | 400 | 488000 | 0.52 | 6.53 | 0 | 238.96 | 24.46
220 | 231 | FGD_150_FVO_eq_ElmLne | ENDKW | Cable | 0.75 | 165 | 123750 | 0.54 | 2.79 | 0 | 507.26 | 11.8
220 | 283 | FGD_150_OSØ_eq_ElmLne | ENDKW | Cable | 1.16 | 165 | 191400 | 0.33 | 2.2 | 0 | 17.17 | 5.8
220 | 299 | FGD_150_SVB_eq_ElmLne | ENDKW | Cable | 0.77 | 165 | 127050 | 1.47 | 12.72 | 0 | 215.2 | 34.5
221 | 232 | FGD_400_FVO_eq_ElmLne | ENDKW | Cable | 2.44 | 400 | 976000 | 0.37 | 4.37 | 0 | 49.9 | 14
221 | 256 | FGD_400_KIN_eq_ElmLne | ENDKW | Cable | 2.44 | 400 | 976000 | 1.04 | 12.4 | 0 | 141.6 | 39.73
221 | 261 | FGD_400_LAG_eq_ElmLne | ENDKW | Cable | 0.92 | 400 | 368000 | 2.11 | 21.57 | 0 | 538.38 | 75.18
226 | 244 | FRD_150_HVO(1)_eq_ElmLne | ENDKW | Cable | 0.96 | 165 | 158400 | 1.62 | 5.53 | 0 | 148.36 | 27
226 | 258 | FRD_150_KLT_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 3.41 | 11.28 | 0 | 80.78 | 28.53
226 | 276 | FRD_150_MOSV_eq_ElmLne | ENDKW | Cable | 0.43 | 165 | 70950 | 6.42 | 21.11 | 0 | 272.59 | 54.5
227 | 228 | FRT_150_FRX_eq_ElmLne | ENDKW | Cable | 10 | 165 | 1650000 | 0 | 0 | 0 | 0 | 0.01
227 | 257 | FRT_150_KLF | ENDKW | Cable | 0.83 | 165 | 136950 | 0.67 | 4.27 | 0 | 1796.99 | 22
227 | 277 | FRT_150_NOR_eq_ElmLne | ENDKW | Cable | 0.88 | 165 | 145200 | 0.45 | 3.09 | 0 | 1226.27 | 15.01
231 | 233 | FVO_150_GRP_eq_ElmLne | ENDKW | Cable | 0.76 | 165 | 125400 | 0.88 | 5.16 | 0 | 2306.68 | 28.24
231 | 283 | FVO_150_OSØ_eq_ElmLne | ENDKW | Cable | 0.75 | 165 | 123750 | 0.37 | 0.69 | 0 | 494.99 | 6.06
231 | 284 | FVO_150_OVE | ENDKW | Cable | 0.75 | 165 | 123750 | 0.59 | 3.41 | 0 | 655.25 | 13.69
233 | 255 | GRP_150_KIN_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 0.28 | 0.74 | 0 | 618.33 | 7.57
289 | 233 | GRP_150_RYT | ENDKW | Cable | 0.75 | 165 | 123750 | 0.92 | 15.82 | 0 | 2450.44 | 30.02
234 | 262 | HASV150_LGB1_eq_ElmLne | ENDKW | Cable | 1.13 | 165 | 186450 | 0.15 | 1.25 | 0 | 681.73 | 7
234 | 274 | HASV150_MLP_eq_ElmLne | ENDKW | Cable | 1.13 | 165 | 186450 | 0.15 | 1.27 | 0 | 691.46 | 7.1
234 | 243 | HAS_150_HSK | ENDKW | Cable | 1.13 | 165 | 186450 | 0.1 | 0.87 | 0 | 474.29 | 4.87
235 | 259 | HAT_150_KNA_eq_ElmLne | ENDKW | Cable | 0.88 | 165 | 145200 | 0.99 | 7.53 | 0 | 352.52 | 27.85
235 | 267 | HAT_150_MAL_eq_ElmLne | ENDKW | Cable | 1.96 | 165 | 323400 | 1.24 | 10.08 | 0 | 132.59 | 34.44
236 | 291 | HER_150_SFE_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 2.82 | 9.55 | 0 | 61.44 | 22.8
236 | 297 | HER_150_STR_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 5.36 | 18.24 | 0 | 123.03 | 44.9
238 | 250 | HNB_150_KAG_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.89 | 7.45 | 0 | 66.05 | 20.96
238 | 321 | HNB_150_TRI_eq_ElmLne | ENDKW | Cable | 0.79 | 165 | 130350 | 0.97 | 7.6 | 0 | 437.05 | 24.45
240 | 249 | HRA_150_KAE_eq_ElmLne | ENDKW | Cable | 0.65 | 165 | 107250 | 2.35 | 6.34 | 0 | 1033.06 | 56.34
243 | 267 | HSKV150_MAL | ENDKW | Cable | 1.13 | 165 | 186450 | 0.25 | 2.11 | 0 | 1149.19 | 11.8
244 | 278 | HVO_150_NSP_eq_ElmLne | ENDKW | Cable | 0.75 | 165 | 123750 | 0.77 | 4.1 | 0 | 1253.5 | 19
244 | 281 | HVO_150_NVV1_eq_ElmLne | ENDKW | Cable | 0.84 | 165 | 138600 | 0.62 | 3.31 | 0 | 25.24 | 8.6
244 | 281 | HVO_150_NVV2_eq_ElmLne | ENDKW | Cable | 0.84 | 165 | 138600 | 0.62 | 3.31 | 0 | 25.24 | 8.6
244 | 296 | HVO_150_SKA_eq_ElmLne | ENDKW | Cable | 0.54 | 165 | 89100 | 0.27 | 1.24 | 0 | 408.81 | 6.33
245 | 276 | HVV_150_MOSV_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 1.41 | 9.96 | 0 | 901.13 | 36.04
246 | 267 | HØN_150_MAL_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.31 | 3.13 | 0 | 43.34 | 10.82
246 | 321 | HØN_150_TRI | ENDKW | Cable | 1.38 | 165 | 227700 | 1.13 | 9.41 | 0 | 83.89 | 26.55
247 | 285 | IDU_150_RAM | ENDKW | Cable | 0.93 | 165 | 153450 | 0.9 | 5.74 | 0 | 2417.77 | 29.6
247 | 297 | IDU_150_STR(1)_eq_ElmLne | ENDKW | Cable | 0.93 | 165 | 153450 | 0.93 | 3.34 | 0 | 227.25 | 16.4
247 | 335 | IDU_150_VID(1)_eq_ElmLne | ENDKW | Cable | 1.44 | 165 | 237600 | 1.75 | 5.98 | 0 | 160.45 | 29.2
248 | 316 | IDU_400_TJE_eq_ElmLne | ENDKW | Cable | 1.2 | 400 | 480000 | 1.64 | 22.37 | 0 | 267.68 | 72.6
249 | 265 | KAE_150_LYK1_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 2.13 | 7.68 | 0 | 537.38 | 21.9
249 | 265 | KAE_150_LYK2_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 2.13 | 7.68 | 0 | 537.38 | 21.9
249 | 265 | KAE_150_LYK3_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 2.18 | 7.89 | 0 | 584.68 | 22.25
249 | 291 | KAE_150_SFE_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 4.71 | 15.97 | 0 | 246.08 | 39.35
249 | 298 | KAE_150_STSV(1)_eq_ElmLne | ENDKW | Cable | 1.34 | 165 | 221100 | 1.74 | 5.94 | 0 | 159.34 | 29
250 | 254 | KAG_150_KBBV_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 0.47 | 1.51 | 0 | 903.21 | 12.5
250 | 307 | KAG_150_THØ_eq_ElmLne | ENDKW | Cable | 0.75 | 165 | 123750 | 0.27 | 0.88 | 0 | -859.49 | 7.26
252 | 266 | KAS_150_MAG_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 1.22 | 11.05 | 0 | 84.03 | 28.75
294 | 252 | KAS_150_SHE1_eq_ElmLne | ENDKW | Cable | 0.57 | 165 | 94050 | 0.37 | 2.37 | 0 | 998.96 | 12.23
252 | 294 | KAS_150_SHE2_eq_ElmLne | ENDKW | Cable | 0.57 | 165 | 94050 | 0.37 | 2.37 | 0 | 998.96 | 12.23
252 | 294 | KAS_150_SHE3 | ENDKW | Cable | 0.57 | 165 | 94050 | 0.37 | 2.37 | 0 | 996.51 | 12.2
253 | 261 | KAS_400_LAG_eq_ElmLne | ENDKW | Cable | 2.76 | 400 | 1104000 | 1.47 | 20.89 | 0 | 244.85 | 67.59
253 | 286 | KAS_400_REV1(1)_eq_ElmLne | ENDKW | Cable | 2.15 | 400 | 860000 | 0.9 | 14.98 | 0 | 530.79 | 54.6
253 | 286 | KAS_400_REV2(1)_eq_ElmLne | ENDKW | Cable | 2.16 | 400 | 864000 | 0.9 | 14.6 | 0 | 533.48 | 54.6
256 | 261 | KIN_400_LAG_eq_ElmLne | ENDKW | Cable | 0.92 | 400 | 368000 | 1.02 | 8.79 | 0 | 395.81 | 34.68
257 | 258 | KLF_150_KLT_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 0.05 | 0.18 | 0 | 1.27 | 0.45
257 | 336 | KLF_150_VIL | ENDKW | Cable | 0.43 | 165 | 70950 | 1.57 | 5.07 | 0 | 194.1 | 14.25
259 | 260 | KNA_150_LAG_eq_ElmLne | ENDKW | Cable | 0.88 | 165 | 145200 | 0.66 | 4.49 | 0 | 556.69 | 19.16
259 | 306 | KNA_150_THY_eq_ElmLne | ENDKW | Cable | 0.98 | 165 | 161700 | 2.16 | 11.56 | 0 | 85.96 | 29.85
260 | 289 | LAG_150_RYT_eq_ElmLne | ENDKW | Cable | 1.13 | 165 | 186450 | 0.41 | 3.62 | 0 | 824.19 | 13.81
260 | 302 | LAG_150_SVS_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.3 | 2.73 | 0 | 20.75 | 7.1
261 | 268 | LAG_400_MAL__eq_ElmLne | ENDKW | Cable | 2.16 | 400 | 864000 | 1.61 | 23.08 | 0 | 522.85 | 77.8
261 | 286 | LAG_400_REV | ENDKW | Cable | 2.16 | 400 | 864000 | 0.37 | 4.36 | 0 | 119.01 | 27.2
261 | 303 | LAG_400_SVS_eq_ElmLne | ENDKW | Cable | 1.2 | 400 | 480000 | 0.16 | 2.24 | 0 | 25.26 | 7.1
262 | 267 | LGB_150_MAL | ENDKW | Cable | 1.38 | 165 | 227700 | 0.66 | 5.51 | 0 | 49.45 | 15.6
262 | 321 | LGB_150_TRI1_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.62 | 5.18 | 0 | 46.5 | 14.67
263 | 298 | LKR_150_STSV | ENDKW | Cable | 1.13 | 165 | 186450 | 0.52 | 4.48 | 0 | 2434.73 | 25
263 | 335 | LKR_150_VID_eq_ElmLne | ENDKW | Cable | 0.9 | 165 | 148500 | 0.56 | 3.82 | 0 | 1494.77 | 18.3
264 | 311 | LOL_150_TJE_eq_ElmLne | ENDKW | Cable | 0.92 | 165 | 151800 | 0.48 | 4.03 | 0 | 107.9 | 11.76
265 | 287 | LYK_150_RIB_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 1.78 | 9.94 | 0 | 270.73 | 27.58
338 | 265 | LYK_150_VKE(1)_eq_ElmLne | ENDKW | Cable | 1.43 | 165 | 235950 | 0.08 | 1.11 | 0 | 164.03 | 4.2
268 | 323 | MAL_400_TRI_eq_ElmLne | ENDKW | Cable | 1.8 | 400 | 720000 | 0.65 | 8.69 | 0 | 117.81 | 30.27
269 | 321 | MES_150_TRI_eq_ElmLne | ENDKW | Cable | 0.59 | 165 | 97350 | 0.88 | 5.34 | 0 | 2262.26 | 28.1
269 | 340 | MES_150_ÅSP_eq_ElmLne | ENDKW | Cable | 0.44 | 165 | 72600 | 1.45 | 3.4 | 0 | 1649.83 | 27.64
272 | 321 | MKS_150_TRI1_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.57 | 4.8 | 0 | 40.74 | 13.2
272 | 321 | MKS_150_TRI2_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.57 | 4.8 | 0 | 40.74 | 13.2
272 | 321 | MKS_150_TRI3(1)_eq_ElmLne | ENDKW | Cable | 2.76 | 165 | 455400 | 0.28 | 2.29 | 0 | 82.71 | 13.3
273 | 323 | MKS_400_TRI_eq_ElmLne | ENDKW | Cable | 1.2 | 400 | 480000 | 0.29 | 3.82 | 0 | 51.76 | 13.3
274 | 321 | MLP_150_TRI_eq_ElmLne | ENDKW | Cable | 1.38 | 165 | 227700 | 0.36 | 3.05 | 0 | 25.87 | 8.4
275 | 321 | MLU_150_TRI_eq_ElmLne | ENDKW | Cable | 1.2 | 165 | 198000 | 0.8 | 6.79 | 0 | 58.24 | 18.8
276 | 311 | MOSV150_TJE(1)_eq_ElmLne | ENDKW | Cable | 1.79 | 165 | 295350 | 2.23 | 7.59 | 0 | 213.57 | 38.6
276 | 336 | MOSV150_VIL_eq_ElmLne | ENDKW | Cable | 0.73 | 165 | 120450 | 3.23 | 10.67 | 0 | 76.45 | 27
281 | 290 | NVV_150_SBA_eq_ElmLne | ENDKW | Cable | 0.65 | 165 | 107250 | 6.2 | 20.9 | 0 | 403.92 | 54.8
281 | 339 | NVV_150_ÅBØ_eq_ElmLne | ENDKW | Cable | 1.04 | 165 | 171600 | 0.11 | 1.06 | 0 | 187.26 | 4
282 | 327 | NVV_400_VHA_eq_ElmLne | ENDKW | Cable | 2.4 | 400 | 960000 | 0.06 | 0.81 | 0 | 10.93 | 2.81
285 | 297 | RAM_150_STR_eq_ElmLne | ENDKW | Cable | 0.72 | 165 | 118800 | 0.9 | 3.05 | 0 | 1622.86 | 24.6
199 | 286 | REV_400_TJE-1_eq_ElmLne | ENDKW | Cable | 4 | 400 | 1600000 | 0.85 | 14 | 0 | 218.38 | 51
199 | 316 | REV_400_TJE-2(1)_eq_ElmLne | ENDKW | Cable | 2.15 | 400 | 860000 | 1.11 | 17.84 | 0 | 1049.18 | 68.9
288 | 295 | RSL_150_SIN | ENDKW | Cable | 0.9 | 165 | 148500 | 0.52 | 3.18 | 0 | 1376.33 | 17.5
289 | 302 | RYT_150_SVS_eq_ElmLne | ENDKW | Cable | 0.58 | 165 | 95700 | 0.56 | 3.53 | 0 | 256.22 | 12.18
294 | 304 | SHE_150_SØN(1)_eq_ElmLne | ENDKW | Cable | 0.86 | 165 | 141900 | 1.83 | 10.01 | 0 | 168.73 | 25.6
294 | 21 | SHE_150_UWN_eq_ElmLne | FLENSBORG | Cable | 0.56 | 165 | 92400 | 1.92 | 9.26 | 0 | 311.32 | 27.28
298 | 335 | STSV150_VID(1)_eq_ElmLne | ENDKW | Cable | 1.44 | 165 | 237600 | 1.31 | 4.47 | 0 | 119.78 | 21.8
311 | 305 | TAN_150_TJE_eq_ElmLne | ENDKW | Cable | 1.02 | 165 | 168300 | 0.29 | 3.03 | 0 | 1151.71 | 14.1
305 | 321 | TAN_150_TRIN(1)_eq_ElmLne | ENDKW | Cable | 1.5 | 165 | 247500 | 2.18 | 13.32 | 0 | 363.58 | 35.7
305 | 321 | TAN_150_TRIS(1)_eq_ElmLne | ENDKW | Cable | 1.5 | 165 | 247500 | 2.17 | 12.83 | 0 | 366.66 | 35.7
321 | 340 | TRI_150_ÅSP_eq_ElmLne | ENDKW | Cable | 0.44 | 165 | 72600 | 2.19 | 7.85 | 0 | 1698.87 | 51.15
326 | 339 | VHA_150_ÅBØ1_eq_ElmLne | ENDKW | Cable | 0.58 | 165 | 95700 | 0.17 | 1.03 | 0 | 413.31 | 5.06

## Transformer2
Transformer2 Data | Energinet.dk | 2020
High.V Bus Index | Low.V Bus Index | 2-Transformer Name | Un.H[kV] | Un.L[kV] | Sn[MVA] | uk[%] | Pcu[kW] | No Load Current[%] | No Load Losses[kW] | Min.Tap | Max.Tap | Neu.Tap | Act.Tap | dU.Tap[%] | dUphase[deg] | Auto.Tap | Control Mode | V.Low Limits[pu] | V.Up Limits[pu] | Control Bus Index
58 | 56 | AMV_132_010_MT1 | 144,0 | 11,0 | 100,0 | 7,07 | 170,0 | 0,06 | 54,8 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
58 | 57 | AMV_132_0173_MT3 | 144,0 | 17,0 | 300,0 | 12,00 | 450,0 | 0,15 | 143,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
61 | 59 | ASV_132_0122_MT2 | 144,1 | 12,0 | 159,0 | 12,20 | 222,6 | 0,60 | 88,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
62 | 61 | ASV_4001_132_T41B | 400,0 | 132,0 | 500,0 | 14,50 | 950,0 | 0,04 | 187,9 | 1 | 27 | 14 | 14 | 0,90 | -180 | Yes | V | 1,01 | 1,03 | 62
63 | 60 | ASV_400_0215_MT5 | 425,0 | 21,0 | 750,0 | 13,90 | 1125,0 | 0,03 | 235,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
63 | 62 | ASV_400_4001_T41A | 400,0 | 400,0 | 500,0 | 0,04 | 50,0 | 0,00 | 0,0 | 1 | 21 | 1 | 2 | 1,09 | -179 | No
69 | 68 | AVV_1321_132_T41B | 132,0 | 132,0 | 53,1 | 0,18 | 37,2 | 0,05 | 27,1 | -8 | 8 | 0 | 0 | 0,00 | 1 | No
68 | 66 | AVV_132_0171_MT1 | 144,0 | 17,0 | 300,0 | 12,00 | 450,0 | 0,15 | 143,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
70 | 67 | AVV_400_0201_MT2 | 425,0 | 19,5 | 558,0 | 12,80 | 669,6 | 0,17 | 250,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
70 | 69 | AVV_400_1321_T41A | 400,0 | 132,0 | 250,0 | 11,33 | 425,0 | 0,04 | 68,7 | 1 | 17 | 9 | 10 | 1,00 | -180 | Yes | V | 1,01 | 1,03 | 70
76 | 77 | BJS_220_2201-T31 | 232,0 | 232,0 | 450,0 | 3,00 | 0,0 | 0,00 | 0,0 | -10 | 10 | 0 | 0 | 1,75 | 90 | No
78 | 74 | BJS_400_016_T45 | 420,0 | 15,8 | 250,0 | 14,00 | 660,0 | 0,26 | 82,0 | 1 | 21 | 11 | 11 | 1,25 | 0 | Yes | V | 0,95 | 1,05 | 74
78 | 75 | BJS_400_132-T42 | 400,0 | 132,0 | 400,0 | 11,83 | 600,0 | 0,03 | 100,5 | 1 | 17 | 9 | 9 | 1,00 | -180 | Yes | V | 1,01 | 1,03 | 78
78 | 75 | BJS_400_132_T41 | 440,0 | 145,0 | 350,0 | 21,86 | 1225,0 | 0,18 | 217,5 | 1 | 27 | 14 | 17 | 1,04 | -180 | Yes | V | 1,01 | 1,03 | 78
78 | 76 | BJS_400_220-T43 | 410,0 | 235,0 | 500,0 | 13,70 | 500,0 | 0,01 | 47,5 | 1 | 21 | 11 | 11 | 1,00 | 0 | Yes | V | 0,95 | 1,04 | 178
99 | 98 | GØR_1321_132_T41B | 132,0 | 132,0 | 85,1 | 0,50 | 76,6 | 0,05 | 41,8 | -8 | 8 | 0 | 0 | 0,00 | 1 | No
100 | 99 | GØR_400_1321_T41A | 400,0 | 132,0 | 400,0 | 11,83 | 600,0 | 0,03 | 100,5 | 1 | 17 | 9 | 9 | 1,00 | -180 | Yes | V | 1,01 | 1,03 | 100
103 | 102 | HCV_400_132_T41 | 400,0 | 132,0 | 350,0 | 13,56 | 665,0 | 0,03 | 73,3 | 1 | 17 | 9 | 7 | 1,00 | -180 | Yes | V | 0,98 | 1,01 | 103
117 | 116 | HVE_400_132_T41 | 440,0 | 145,0 | 350,0 | 21,81 | 1260,0 | 0,21 | 217,8 | 1 | 27 | 14 | 17 | 1,04 | -180 | Yes | V | 1,01 | 1,03 | 117
117 | 116 | HVE_400_132_T44 | 400,0 | 132,0 | 500,0 | 25,83 | 1750,0 | 0,09 | 191,0 | 1 | 27 | 14 | 17 | 1,02 | -180 | Yes | V | 1,01 | 1,03 | 117
122 | 120 | ISH_400_132_T41 | 400,0 | 132,0 | 500,0 | 26,75 | 1550,0 | 0,20 | 155,7 | 1 | 27 | 14 | 17 | 1,07 | -180 | Yes | V | 1,01 | 1,03 | 122
122 | 121 | ISH_400_220-T42 | 410,0 | 235,0 | 500,0 | 13,70 | 500,0 | 0,01 | 47,5 | 1 | 21 | 11 | 11 | 1,00 | 0 | Yes | V | 0,00 | 1,05 | 121
132 | 131 | KFE_010_000-T12 | 10,0 | 0,4 | 1,0 | 5,25 | 0,7 | 0,32 | 1,0 | -2 | 2 | 0 | 0 | 2,50 | 0 | No
145 | 141 | KYV_132_0181_MT21 | 141,3 | 18,0 | 307,0 | 12,69 | 644,7 | 0,04 | 60,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
145 | 143 | KYV_132_0182_MT22 | 141,3 | 18,0 | 330,0 | 12,80 | 660,0 | 0,04 | 60,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
147 | 146 | LIN_132_132_T13 | 132,0 | 132,0 | 125,0 | 3,91 | 250,0 | 0,09 | 27,9 | -8 | 8 | 0 | 0 | 0,00 | 1 | Yes | V | 0,95 | 1,05 | 147
161 | 160 | RAD_132_009_T1 | 132,0 | 9,0 | 80,2 | 9,35 | 745,9 | 0,10 | 20,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
176 | 175 | STV_132_0182_MT2 | 144,3 | 18,0 | 310,0 | 12,60 | 713,0 | 0,30 | 172,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
190 | 189 | ØSV_400_132-KT41 | 400,0 | 132,0 | 400,0 | 11,83 | 600,0 | 0,03 | 100,5 | 1 | 17 | 9 | 14 | 1,00 | -180 | Yes | V | 1,01 | 1,03 | 190
192 | 193 | ABS_1501_150_KT31 | 165,0 | 165,0 | 350,0 | 2,31 | 59,1 | 0,09 | 29,8 | -10 | 10 | 0 | 0 | 0,00 | 1 | No
198 | 197 | ASR_400_150_KT51 | 410,0 | 167,7 | 200,0 | 13,17 | 440,0 | 0,06 | 40,2 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 197
214 | 210 | EDR_400_150C_KT52 | 410,0 | 167,6 | 400,0 | 12,65 | 1120,0 | 0,03 | 79,0 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,98 | 1,02 | 241
214 | 211 | EDR_400_220-KT54 | 410,0 | 238,3 | 450,0 | 13,70 | 625,3 | 0,03 | 45,7 | 1 | 21 | 11 | 9 | 1,01 | 0 | Yes | V | 1,03 | 0,97 | 211
217 | 216 | FER_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,63 | 1000,0 | 0,03 | 73,5 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 216
221 | 220 | FGD_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,59 | 1000,0 | 0,03 | 71,5 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 220
221 | 220 | FGD_400_150_KT52 | 410,0 | 167,6 | 400,0 | 12,59 | 1000,0 | 0,03 | 71,5 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 220
231 | 229 | FVO_150_010_MT1 | 165,0 | 10,5 | 45,0 | 14,93 | 117,0 | 0,15 | 24,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
232 | 230 | FVO_400_021A_MT51 | 433,0 | 21,0 | 455,0 | 15,21 | 728,0 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
294 | 237 | HER_060_012_MT21 | 165,0 | 11,5 | 102,0 | 12,07 | 315,6 | 0,73 | 48,7 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
248 | 247 | IDU_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,68 | 960,0 | 0,03 | 79,0 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 247
253 | 252 | KAS_400_150_KT51 | 410,0 | 167,6 | 400,0 | 13,02 | 1000,0 | 0,03 | 108,4 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 252
253 | 252 | KAS_400_150_KT52 | 410,0 | 167,6 | 400,0 | 12,68 | 960,0 | 0,03 | 79,0 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 252
256 | 255 | KIN_400_150_KT51 | 410,0 | 167,7 | 200,0 | 13,17 | 440,0 | 0,06 | 39,8 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 255
261 | 260 | LAG_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,59 | 1000,0 | 0,03 | 73,8 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 260
268 | 267 | MAL_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,66 | 960,0 | 0,03 | 73,5 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 267
272 | 270 | MKS_150_019A_MT31 | 173,0 | 19,0 | 455,0 | 13,70 | 819,0 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
273 | 271 | MKS_400_019B_MT51 | 428,0 | 19,0 | 455,0 | 14,20 | 819,0 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
281 | 280 | NVV_150_021B_MT31 | 165,0 | 21,0 | 350,0 | 12,20 | 735,0 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
282 | 279 | NVV_400_021A_MT51 | 421,3 | 21,0 | 485,0 | 12,80 | 824,5 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
282 | 281 | NVV_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,58 | 960,0 | 0,03 | 69,7 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 281
294 | 292 | SHE_150_021_MT31 | 174,0 | 21,0 | 890,0 | 18,85 | 1691,0 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
303 | 300 | SVS_400_021_MT51 | 429,4 | 21,0 | 485,0 | 13,00 | 824,5 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
308 | 309 | TJE_010_010_HT3 | 6,0 | 6,0 | 1,0 | 3,00 | 0,0 | 0,00 | 0,0 | 0 | 0 | 0 | 0 | 0,00 | 0 | No
312 | 310 | TJE_150_013_MT31 | 167,0 | 12,5 | 180,0 | 6,36 | 540,0 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No
316 | 311 | TJE_400_150_KT51 | 410,0 | 167,6 | 400,0 | 13,02 | 1000,0 | 0,03 | 108,4 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 311
323 | 321 | TRI_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,61 | 1000,0 | 0,03 | 90,0 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 321
323 | 322 | TRI_400_220_KT53 | 410,0 | 238,3 | 450,0 | 13,66 | 625,3 | 0,03 | 45,7 | 1 | 21 | 11 | 9 | 1,00 | 0 | Yes | V | 0,98 | 1,02 | 195
323 | 322 | TRI_400_220_KT54 | 410,0 | 238,3 | 450,0 | 13,70 | 654,9 | 0,03 | 44,3 | 1 | 21 | 11 | 9 | 1,00 | 0 | Yes | V | 0,98 | 1,02 | 195
327 | 326 | VHA_400_150_KT51 | 410,0 | 167,6 | 400,0 | 12,60 | 595,1 | 0,03 | 64,2 | 1 | 21 | 11 | 9 | 1,76 | 0 | Yes | V | 0,97 | 1,01 | 326
338 | 337 | VKE_150_019_MT31 | 175,7 | 19,0 | 457,5 | 11,78 | 640,5 | 0,00 | 0,0 | 1 | 1 | 1 | 1 | 0,00 | 0 | No

## Transformer3
Transformer3 Data | Energinet.dk | 2020
High.V Bus Index | Mid.V Bus Index | Low.V Bus Index | 3_Transformer Name | Un.H[kV] | Un.M[kV] | Un.L[kV] | Sn[MVA] | uk.HV_MV[%] | uk.MV_LV[%] | uk.LV_HV[%] | Pcu.HV_MV[kW] | Pcu.MV_LV[kW] | Pcu.LV_HV[kW] | No Load Current[%] | No Load Losses[kW] | Tap Side | Min.Tap | Max.Tap | Neu.Tap | Act.Tap | dU.Tap[%] | dUphase.Tap[deg] | Auto.Tap | Control Mode | Voltage min[pu] | Voltage max[pu] | Control Bus Index
70 | 64 | 65 | AVV_400_0123_0122_MTG | 425,00 | 11,50 | 11,50 | 270,00 | 38,25 | 72,00 | 38,52 | 1425,51 | 0,00 | 1496,52 | 0,19 | 111,50 | HV | 0 | 0 | 0 | 0 | 0,00 | 0,00 | No
96 | 95 | 93 | GLN_400_132_010D_T41 | 400,00 | 132,00 | 9,83 | 350,00 | 13,53 | 56,69 | 74,86 | 665,00 | 12530,00 | 11935,00 | 0,02 | 72,34 | HV | 1 | 17 | 9 | 7 | 1,00 | 180,00 | Yes | V | 0,99 | 1,02 | 96
96 | 95 | 94 | GLN_400_132_010D_T42 | 400,00 | 132,00 | 9,83 | 350,00 | 13,57 | 56,69 | 74,86 | 630,00 | 12390,00 | 11900,00 | 0,03 | 74,74 | HV | 1 | 17 | 9 | 7 | 1,00 | 180,00 | Yes | V | 0,99 | 1,02 | 96
108 | 107 | 106 | HKS_400_016_010_MT1 | 400,00 | 15,75 | 10,00 | 255,00 | 10,99 | 89,25 | 74,46 | 571,70 | 7282,80 | 6762,60 | 0,05 | 87,73 | HV | 0 | 0 | 0 | 0 | 0,00 | 0,00 | No
134 | 133 | 132 | KFE_220_150_010-T31--$ | 232,00 | 165,00 | 10,00 | 450,00 | 13,53 | 56,69 | 74,86 | 665,00 | 12530,00 | 11935,00 | 0,02 | 72,34 | HV | 1 | 17 | 9 | 9 | 1,00 | 180,00 | Yes | V | 0,99 | 1,01 | 134
145 | 137 | 139 | KYV_132_0102_0103_MT1 | 139,50 | 11,00 | 11,00 | 158,00 | 18,00 | 33,40 | 17,80 | 775,20 | 1423,60 | 754,80 | 0,19 | 105,24 | HV | 0 | 0 | 0 | 0 | 0,00 | 0,00 | No
214 | 209 | 208 | EDR_400_150_015_KT51 | 410,00 | 167,40 | 15,00 | 400,00 | 12,61 | 36,23 | 51,74 | 675,55 | 693,33 | 711,20 | 0,03 | 75,11 | MV | 1 | 21 | 11 | 9 | 1,74 | 0,00 | Yes | V | 0,97 | 1,01 | 209
221 | 219 | 218 | FGD_400_016_010_MT1 | 400,00 | 15,75 | 10,00 | 255,00 | 11,06 | 89,25 | 73,95 | 571,60 | 7282,80 | 6762,60 | 0,05 | 88,62 | HV | 0 | 0 | 0 | 0 | 0,00 | 0,00 | No
316 | 312 | 309 | TJE_400_150_010_KT52 | 410,00 | 167,57 | 10,03 | 600,00 | 12,70 | 840,00 | 852,00 | 1060,00 | 69999,99 | 71000,01 | 0,03 | 97,00 | MV | 1 | 21 | 11 | 9 | 1,71 | 0,00 | Yes | V | 0,97 | 1,01 | 312
326 | 325 | 324 | VHA_150_012_010_KT31 | 165,00 | 11,60 | 10,44 | 125,00 | 12,53 | 48,86 | 65,00 | 312,50 | 7150,00 | 6175,00 | 0,07 | 44,25 | LV | 1 | 10 | 9 | 9 | 3,22 | 180,00 | No

## Generator
Generator Data | Energinet.dk | 2020
Bus Index | Generator Name | Control Type | Nominal Apparent Power[MVA] | Nominal Voltage[kV] | Pmin[MW] | Pmax[MW] | Qmin[Mvar] | Qmax[Mvar] | Act.P[MW] | Act.Q[Mvar] | Control Bus Index | Uref[pu]
53 | ALL_132_WindOn | PQ | 5,41 | 132,00 | 0,00 | 3,90 | -5,41 | 5,41 | 0,03 | 0,00
53 | ALL_132_gas | PQ | 88,23 | 132,00 | 0,00 | 63,53 | -88,23 | 88,23 | 21,18 | 0,00
53 | ALL_132_solar | PQ | 10,51 | 132,00 | 0,00 | 7,57 | -10,51 | 10,51 | 0,00 | 0,00
55 | AMK_132_WindOn | PQ | 0,94 | 132,00 | 0,00 | 0,68 | -0,94 | 0,94 | 0,01 | 0,00
55 | AMK_132_gas | PQ | 1,02 | 132,00 | 0,00 | 0,74 | -1,02 | 1,02 | 0,25 | 0,00
55 | AMK_132_solar | PQ | 4,59 | 132,00 | 0,00 | 3,30 | -4,59 | 4,59 | 0,00 | 0,00
56 | s_AMV1 | PV | 100,71 | 10,50 | 0,00 | 71,00 | -52,00 | 80,00 | 39,32 | 0,00 | 58 | 1,00
57 | s_AMV3.1 | PV | 176,47 | 17,00 | 59,00 | 150,00 | -58,24 | 92,35 | 113,00 | 0,00 | 58 | 1,00
58 | AMV_132_WindOff | PQ | 44,44 | 132,00 | 0,00 | 32,00 | -44,44 | 44,44 | 0,74 | 0,00
58 | AMV_132_WindOn | PQ | 11,33 | 132,00 | 0,00 | 8,16 | -11,33 | 11,33 | 0,07 | 0,00
58 | AMV_132_gas | PQ | 9,44 | 132,00 | 0,00 | 6,80 | -9,44 | 9,44 | 2,27 | 0,00
58 | AMV_132_other | PQ | 22,22 | 132,00 | 0,00 | 16,00 | -22,22 | 22,22 | 15,89 | 0,00
58 | AMV_132_solar | PQ | 0,94 | 132,00 | 0,00 | 0,68 | -0,94 | 0,94 | 0,00 | 0,00
59 | s_ASV2 | PV | 175,00 | 12,00 | 40,00 | 140,00 | -87,50 | 131,25 | 140,00 | 0,00 | 61 | 1,02
61 | ASV_132_WindOff | PQ | 111,10 | 132,00 | 0,00 | 100,00 | -111,10 | 111,10 | 1,84 | 0,00
64 | s_AVV2/G1 | PV | 68,40 | 11,50 | 0,00 | 58,00 | -10,30 | 10,30 | 33,55 | 0,00 | 70 | 1,03
65 | s_AVV2/G2 | PV | 68,40 | 11,50 | 0,00 | 58,00 | -10,30 | 10,30 | 33,55 | 0,00 | 70 | 1,03
66 | s_AVV1 | PV | 294,12 | 17,00 | 55,00 | 250,00 | -147,12 | 220,68 | 239,00 | 0,00 | 68 | 1,02
67 | s_AVV2/DT | SL | 565,00 | 19,50 | 135,00 | 550,00 | -325,00 | 487,50 | 294,88 | 0,00 | 70 | 1,03
71 | BAG_132_WindOn | PQ | 0,01 | 132,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
71 | BAG_132_gas | PQ | 5,89 | 132,00 | 0,00 | 4,24 | -5,89 | 5,89 | 1,41 | 0,00
71 | BAG_132_solar | PQ | 6,84 | 132,00 | 0,00 | 4,93 | -6,84 | 6,84 | 0,00 | 0,00
72 | BAL_132_gas | PQ | 2,48 | 132,00 | 0,00 | 1,78 | -2,48 | 2,48 | 0,59 | 0,00
72 | BAL_132_solar | PQ | 0,07 | 132,00 | 0,00 | 0,05 | -0,07 | 0,07 | 0,00 | 0,00
73 | BEL_132_solar | PQ | 1,88 | 132,00 | 0,00 | 1,35 | -1,88 | 1,88 | 0,00 | 0,00
74 | s_BJS1 | PV | 270,00 | 15,75 | 0,00 | 0,00 | -140,00 | 270,00 | 0,00 | 0,10 | 78 | 1,03
82 | BLA_132_WindOn | PQ | 40,64 | 132,00 | 0,00 | 29,27 | -40,64 | 40,64 | 0,24 | 0,00
82 | BLA_132_gas | PQ | 40,92 | 132,00 | 0,00 | 29,47 | -40,92 | 40,92 | 9,82 | 0,00
82 | BLA_132_solar | PQ | 12,54 | 132,00 | 0,00 | 9,03 | -12,54 | 12,54 | 0,00 | 0,00
83 | BOR_132_WindOn | PQ | 7,66 | 132,00 | 0,00 | 5,51 | -7,66 | 7,66 | 0,05 | 0,00
83 | BOR_132_gas | PQ | 45,36 | 132,00 | 0,00 | 32,66 | -45,36 | 45,36 | 10,89 | 0,00
83 | BOR_132_solar | PQ | 11,75 | 132,00 | 0,00 | 8,46 | -11,75 | 11,75 | 0,00 | 0,00
84 | BRY_132_WindOff | PQ | 12,00 | 132,00 | 0,00 | 8,64 | -12,00 | 12,00 | 0,20 | 0,00
84 | BRY_132_WindOn | PQ | 2,20 | 132,00 | 0,00 | 1,58 | -2,20 | 2,20 | 0,01 | 0,00
84 | BRY_132_solar | PQ | 5,69 | 132,00 | 0,00 | 4,10 | -5,69 | 5,69 | 0,00 | 0,00
87 | DYR_132_WindOn | PQ | 0,08 | 132,00 | 0,00 | 0,06 | -0,08 | 0,08 | 0,00 | 0,00
87 | DYR_132_solar | PQ | 0,65 | 132,00 | 0,00 | 0,47 | -0,65 | 0,65 | 0,00 | 0,00
88 | EBY_132_gas | PQ | 3,44 | 132,00 | 0,00 | 2,48 | -3,44 | 3,44 | 0,83 | 0,00
88 | EBY_132_other | PQ | 45,04 | 132,00 | 0,00 | 32,43 | -45,04 | 45,04 | 32,22 | 0,00
88 | EBY_132_solar | PQ | 4,46 | 132,00 | 0,00 | 3,21 | -4,46 | 4,46 | 0,00 | 0,00
89 | ESK_132_WindOn | PQ | 21,13 | 132,00 | 0,00 | 15,21 | -21,13 | 21,13 | 0,13 | 0,00
89 | ESK_132_gas | PQ | 27,55 | 132,00 | 0,00 | 19,84 | -27,55 | 27,55 | 6,61 | 0,00
89 | ESK_132_solar | PQ | 4,37 | 132,00 | 0,00 | 3,15 | -4,37 | 4,37 | 0,00 | 0,00
91 | FLA_132_solar | PQ | 0,01 | 132,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
92 | FNM_132_solar | PQ | 0,84 | 132,00 | 0,00 | 0,60 | -0,84 | 0,84 | 0,00 | 0,00
95 | GLN_132_gas | PQ | 55,16 | 132,00 | 0,00 | 39,72 | -55,16 | 55,16 | 13,24 | 0,00
95 | GLN_132_solar | PQ | 6,89 | 132,00 | 0,00 | 4,96 | -6,89 | 6,89 | 0,00 | 0,00
97 | GRN_132_solar | PQ | 0,01 | 132,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
98 | GØR_132_solar | PQ | 0,07 | 132,00 | 0,00 | 0,05 | -0,07 | 0,07 | 0,00 | 0,00
101 | HASØ132_WindOn | PQ | 24,89 | 132,00 | 0,00 | 17,92 | -24,89 | 24,89 | 0,15 | 0,00
101 | HASØ132_gas | PQ | 14,86 | 132,00 | 0,00 | 10,70 | -14,86 | 14,86 | 3,57 | 0,00
101 | HASØ132_solar | PQ | 5,56 | 132,00 | 0,00 | 4,00 | -5,56 | 5,56 | 0,00 | 0,00
102 | HCV_132_gas | PQ | 44,44 | 132,00 | 0,00 | 32,00 | -44,44 | 44,44 | 10,67 | 0,00
102 | HCV_132_solar | PQ | 0,72 | 132,00 | 0,00 | 0,52 | -0,72 | 0,72 | 0,00 | 0,00
104 | HDE_132_WindOn | PQ | 1,66 | 132,00 | 0,00 | 1,19 | -1,66 | 1,66 | 0,01 | 0,00
104 | HDE_132_gas | PQ | 23,44 | 132,00 | 0,00 | 16,88 | -23,44 | 23,44 | 5,63 | 0,00
104 | HDE_132_other | PQ | 15,22 | 132,00 | 0,00 | 10,96 | -15,22 | 15,22 | 10,89 | 0,00
104 | HDE_132_solar | PQ | 2,04 | 132,00 | 0,00 | 1,47 | -2,04 | 2,04 | 0,00 | 0,00
105 | HEJ_132_WindOn | PQ | 66,14 | 132,00 | 0,00 | 47,63 | -66,14 | 66,14 | 0,40 | 0,00
105 | HEJ_132_gas | PQ | 17,57 | 132,00 | 0,00 | 12,66 | -17,57 | 17,57 | 4,22 | 0,00
105 | HEJ_132_solar | PQ | 9,39 | 132,00 | 0,00 | 6,76 | -9,39 | 9,39 | 0,00 | 0,00
107 | s_HKS1 | PV | 200,00 | 15,75 | 0,00 | 0,00 | -120,00 | 200,00 | 0,00 | 0,10 | 108 | 1,03
113 | HMA_132_solar | PQ | 1,31 | 132,00 | 0,00 | 0,94 | -1,31 | 1,31 | 0,00 | 0,00
114 | HSKØ132_gas | PQ | 1,89 | 132,00 | 0,00 | 1,36 | -1,89 | 1,89 | 0,45 | 0,00
114 | HSKØ132_solar | PQ | 0,01 | 132,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
118 | IDE_132_WindOn | PQ | 18,21 | 132,00 | 0,00 | 13,11 | -18,21 | 18,21 | 0,11 | 0,00
118 | IDE_132_solar | PQ | 2,41 | 132,00 | 0,00 | 1,74 | -2,41 | 2,41 | 0,00 | 0,00
123 | JER_132_WindOn | PQ | 6,00 | 132,00 | 0,00 | 4,32 | -6,00 | 6,00 | 0,04 | 0,00
123 | JER_132_gas | PQ | 38,36 | 132,00 | 0,00 | 27,62 | -38,36 | 38,36 | 9,21 | 0,00
123 | JER_132_solar | PQ | 6,32 | 132,00 | 0,00 | 4,55 | -6,32 | 6,32 | 0,00 | 0,00
124 | KAK_132_gas | PQ | 0,26 | 132,00 | 0,00 | 0,18 | -0,26 | 0,26 | 0,06 | 0,00
124 | KAK_132_solar | PQ | 0,04 | 132,00 | 0,00 | 0,03 | -0,04 | 0,04 | 0,00 | 0,00
125 | KAM_132_WindOn | PQ | 6,32 | 132,00 | 0,00 | 4,55 | -6,32 | 6,32 | 0,04 | 0,00
125 | KAM_132_gas | PQ | 23,45 | 132,00 | 0,00 | 16,88 | -23,45 | 23,45 | 5,63 | 0,00
125 | KAM_132_solar | PQ | 8,78 | 132,00 | 0,00 | 6,32 | -8,78 | 8,78 | 0,00 | 0,00
127 | KBG_132_WindOn | PQ | 0,38 | 132,00 | 0,00 | 0,27 | -0,38 | 0,38 | 0,00 | 0,00
127 | KBG_132_solar | PQ | 2,57 | 132,00 | 0,00 | 1,85 | -2,57 | 2,57 | 0,00 | 0,00
129 | KFA_220 | PQ | 222,20 | 232,00 | 0,00 | 160,00 | -222,20 | 222,20 | 3,69 | 0,00
130 | KFB_220 | PQ | 444,40 | 232,00 | 0,00 | 320,00 | -444,40 | 444,40 | 3,82 | 0,00
135 | KRL_132_WindOn | PQ | 2,07 | 132,00 | 0,00 | 1,49 | -2,07 | 2,07 | 0,01 | 0,00
135 | KRL_132_gas | PQ | 0,67 | 132,00 | 0,00 | 0,48 | -0,67 | 0,67 | 0,16 | 0,00
135 | KRL_132_solar | PQ | 1,04 | 132,00 | 0,00 | 0,75 | -1,04 | 1,04 | 0,00 | 0,00
136 | KSV_132_WindOn | PQ | 4,26 | 132,00 | 0,00 | 3,07 | -4,26 | 4,26 | 0,03 | 0,00
136 | KSV_132_gas | PQ | 3,42 | 132,00 | 0,00 | 2,46 | -3,42 | 3,42 | 0,82 | 0,00
136 | KSV_132_solar | PQ | 2,03 | 132,00 | 0,00 | 1,46 | -2,03 | 2,03 | 0,00 | 0,00
145 | KYV_132_LightOil | PQ | 22,22 | 132,00 | 0,00 | 16,00 | -22,22 | 22,22 | 0,00 | 0,00
146 | LIN_132_WindOn | PQ | 0,01 | 132,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
146 | LIN_132_solar | PQ | 2,98 | 132,00 | 0,00 | 2,15 | -2,98 | 2,98 | 0,00 | 0,00
148 | LUP_132_WindOn | PQ | 3,23 | 132,00 | 0,00 | 2,33 | -3,23 | 3,23 | 0,02 | 0,00
148 | LUP_132_solar | PQ | 0,76 | 132,00 | 0,00 | 0,55 | -0,76 | 0,76 | 0,00 | 0,00
149 | MAV_132_LightOil | PQ | 77,77 | 132,00 | 0,00 | 56,00 | -77,77 | 77,77 | 0,00 | 0,00
149 | MAV_132_solar | PQ | 0,03 | 132,00 | 0,00 | 0,02 | -0,03 | 0,03 | 0,00 | 0,00
151 | MÅLØ132_WindOn | PQ | 0,01 | 132,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
151 | MÅLØ132_gas | PQ | 15,73 | 132,00 | 0,00 | 11,33 | -15,73 | 15,73 | 3,78 | 0,00
151 | MÅLØ132_solar | PQ | 0,01 | 132,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
152 | NAM_132_WindOn | PQ | 19,03 | 132,00 | 0,00 | 13,70 | -19,03 | 19,03 | 0,11 | 0,00
152 | NAM_132_gas | PQ | 14,53 | 132,00 | 0,00 | 10,46 | -14,53 | 14,53 | 3,49 | 0,00
152 | NAM_132_solar | PQ | 5,39 | 132,00 | 0,00 | 3,88 | -5,39 | 5,39 | 0,00 | 0,00
153 | NSV_132_WindOn | PQ | 39,85 | 132,00 | 0,00 | 28,70 | -39,85 | 39,85 | 0,24 | 0,00
153 | NSV_132_gas | PQ | 4,31 | 132,00 | 0,00 | 3,10 | -4,31 | 4,31 | 1,04 | 0,00
153 | NSV_132_solar | PQ | 4,45 | 132,00 | 0,00 | 3,20 | -4,45 | 4,45 | 0,00 | 0,00
154 | NVS_132_WindOn | PQ | 16,36 | 132,00 | 0,00 | 11,78 | -16,36 | 16,36 | 0,10 | 0,00
154 | NVS_132_gas | PQ | 4,42 | 132,00 | 0,00 | 3,18 | -4,42 | 4,42 | 1,06 | 0,00
154 | NVS_132_solar | PQ | 5,23 | 132,00 | 0,00 | 3,77 | -5,23 | 5,23 | 0,00 | 0,00
155 | NYM_132_gas | PQ | 0,43 | 132,00 | 0,00 | 0,31 | -0,43 | 0,43 | 0,10 | 0,00
155 | NYM_132_solar | PQ | 2,01 | 132,00 | 0,00 | 1,45 | -2,01 | 2,01 | 0,00 | 0,00
157 | NYR_132_WindOn | PQ | 12,05 | 132,00 | 0,00 | 8,67 | -12,05 | 12,05 | 0,07 | 0,00
157 | NYR_132_gas | PQ | 8,55 | 132,00 | 0,00 | 6,16 | -8,55 | 8,55 | 2,05 | 0,00
157 | NYR_132_solar | PQ | 3,18 | 132,00 | 0,00 | 2,29 | -3,18 | 3,18 | 0,00 | 0,00
158 | ORH_132_solar | PQ | 0,26 | 132,00 | 0,00 | 0,19 | -0,26 | 0,26 | 0,00 | 0,00
159 | OST_132_solar | PQ | 0,01 | 132,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
161 | RAD_132_WindOn | PQ | 45,76 | 132,00 | 0,00 | 32,95 | -45,76 | 45,76 | 0,28 | 0,00
161 | RAD_132_gas | PQ | 14,44 | 132,00 | 0,00 | 10,40 | -14,44 | 14,44 | 3,47 | 0,00
161 | RAD_132_solar | PQ | 4,75 | 132,00 | 0,00 | 3,42 | -4,75 | 4,75 | 0,00 | 0,00
162 | RBY_132_WindOn | PQ | 85,10 | 132,00 | 0,00 | 61,28 | -85,10 | 85,10 | 0,51 | 0,00
162 | RBY_132_solar | PQ | 5,94 | 132,00 | 0,00 | 4,27 | -5,94 | 5,94 | 0,00 | 0,00
163 | RDB_132_WindOff | PQ | 229,98 | 132,00 | 0,00 | 165,60 | -229,98 | 229,98 | 3,82 | 0,00
164 | RDS_132_WindOff | PQ | 183,98 | 132,00 | 0,00 | 132,48 | -183,98 | 183,98 | 3,06 | 0,00
166 | RIN_132_WindOn | PQ | 8,53 | 132,00 | 0,00 | 6,14 | -8,53 | 8,53 | 0,05 | 0,00
166 | RIN_132_gas | PQ | 13,39 | 132,00 | 0,00 | 9,64 | -13,39 | 13,39 | 3,21 | 0,00
166 | RIN_132_solar | PQ | 3,75 | 132,00 | 0,00 | 2,70 | -3,75 | 3,75 | 0,00 | 0,00
167 | SIB_132_WindOn | PQ | 2,10 | 132,00 | 0,00 | 1,51 | -2,10 | 2,10 | 0,01 | 0,00
167 | SIB_132_gas | PQ | 1,02 | 132,00 | 0,00 | 0,74 | -1,02 | 1,02 | 0,25 | 0,00
167 | SIB_132_solar | PQ | 1,76 | 132,00 | 0,00 | 1,27 | -1,76 | 1,76 | 0,00 | 0,00
169 | SMK_132_WindOn | PQ | 0,00 | 132,00 | 0,00 | 0,00 | -0,00 | 0,00 | 0,00 | 0,00
169 | SMK_132_solar | PQ | 0,84 | 132,00 | 0,00 | 0,60 | -0,84 | 0,84 | 0,00 | 0,00
171 | SPA_132_WindOn | PQ | 2,34 | 132,00 | 0,00 | 1,68 | -2,34 | 2,34 | 0,01 | 0,00
171 | SPA_132_gas | PQ | 12,80 | 132,00 | 0,00 | 9,21 | -12,80 | 12,80 | 3,07 | 0,00
171 | SPA_132_solar | PQ | 2,49 | 132,00 | 0,00 | 1,79 | -2,49 | 2,49 | 0,00 | 0,00
173 | STA_132_WindOn | PQ | 0,01 | 132,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
173 | STA_132_gas | PQ | 15,57 | 132,00 | 0,00 | 11,21 | -15,57 | 15,57 | 3,74 | 0,00
173 | STA_132_solar | PQ | 3,21 | 132,00 | 0,00 | 2,31 | -3,21 | 3,21 | 0,00 | 0,00
174 | STSØ132_WindOn | PQ | 20,00 | 132,00 | 0,00 | 14,40 | -20,00 | 20,00 | 0,12 | 0,00
176 | STV_132_WindOff | PQ | 111,10 | 132,00 | 0,00 | 100,00 | -111,10 | 111,10 | 1,84 | 0,00
176 | STV_132_WindOn | PQ | 25,85 | 132,00 | 0,00 | 18,62 | -25,85 | 25,85 | 0,16 | 0,00
176 | STV_132_gas | PQ | 14,11 | 132,00 | 0,00 | 10,16 | -14,11 | 14,11 | 3,39 | 0,00
176 | STV_132_solar | PQ | 4,65 | 132,00 | 0,00 | 3,35 | -4,65 | 4,65 | 0,00 | 0,00
177 | TEG_132_WindOn | PQ | 0,09 | 132,00 | 0,00 | 0,07 | -0,09 | 0,09 | 0,00 | 0,00
177 | TEG_132_gas | PQ | 67,77 | 132,00 | 0,00 | 48,80 | -67,77 | 67,77 | 16,27 | 0,00
177 | TEG_132_hydro | PQ | 0,02 | 132,00 | 0,00 | 0,02 | -0,02 | 0,02 | 0,02 | 0,00
177 | TEG_132_solar | PQ | 7,54 | 132,00 | 0,00 | 5,43 | -7,54 | 7,54 | 0,00 | 0,00
179 | TOR_132_WindOn | PQ | 48,44 | 132,00 | 0,00 | 34,88 | -48,44 | 48,44 | 0,29 | 0,00
179 | TOR_132_gas | PQ | 8,66 | 132,00 | 0,00 | 6,24 | -8,66 | 8,66 | 2,08 | 0,00
179 | TOR_132_solar | PQ | 8,48 | 132,00 | 0,00 | 6,10 | -8,48 | 8,48 | 0,00 | 0,00
180 | VAL_132_solar | PQ | 0,03 | 132,00 | 0,00 | 0,02 | -0,03 | 0,03 | 0,00 | 0,00
182 | VEJ_132_WindOn | PQ | 0,97 | 132,00 | 0,00 | 0,70 | -0,97 | 0,97 | 0,01 | 0,00
182 | VEJ_132_gas | PQ | 2,83 | 132,00 | 0,00 | 2,04 | -2,83 | 2,83 | 0,68 | 0,00
182 | VEJ_132_solar | PQ | 5,28 | 132,00 | 0,00 | 3,80 | -5,28 | 5,28 | 0,00 | 0,00
183 | VIK_132_WindOn | PQ | 0,50 | 132,00 | 0,00 | 0,36 | -0,50 | 0,50 | 0,00 | 0,00
183 | VIK_132_gas | PQ | 0,61 | 132,00 | 0,00 | 0,44 | -0,61 | 0,61 | 0,15 | 0,00
183 | VIK_132_solar | PQ | 2,25 | 132,00 | 0,00 | 1,62 | -2,25 | 2,25 | 0,00 | 0,00
184 | VIN_132_solar | PQ | 0,01 | 132,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
185 | VLO_132_WindOn | PQ | 107,08 | 132,00 | 0,00 | 77,11 | -107,08 | 107,08 | 0,64 | 0,00
185 | VLO_132_gas | PQ | 17,78 | 132,00 | 0,00 | 12,80 | -17,78 | 17,78 | 4,27 | 0,00
185 | VLO_132_solar | PQ | 8,62 | 132,00 | 0,00 | 6,20 | -8,62 | 8,62 | 0,00 | 0,00
187 | ØLS_132_WindOn | PQ | 0,08 | 132,00 | 0,00 | 0,05 | -0,08 | 0,08 | 0,00 | 0,00
187 | ØLS_132_gas | PQ | 3,10 | 132,00 | 0,00 | 2,24 | -3,10 | 3,10 | 0,75 | 0,00
187 | ØLS_132_solar | PQ | 6,87 | 132,00 | 0,00 | 4,95 | -6,87 | 6,87 | 0,00 | 0,00
188 | ØSH_132_OCGTOld | PQ | 14,44 | 132,00 | 0,00 | 10,40 | -14,44 | 14,44 | 13,00 | 0,00
188 | ØSH_132_WindOn | PQ | 8,72 | 132,00 | 0,00 | 6,28 | -8,72 | 8,72 | 0,05 | 0,00
188 | ØSH_132_gas | PQ | 2,74 | 132,00 | 0,00 | 1,97 | -2,74 | 2,74 | 0,66 | 0,00
188 | ØSH_132_hydro | PQ | 0,00 | 132,00 | 0,00 | 0,00 | -0,00 | 0,00 | 0,00 | 0,00
188 | ØSH_132_solar | PQ | 2,07 | 132,00 | 0,00 | 1,49 | -2,07 | 2,07 | 0,00 | 0,00
192 | ABS_150_WindOn | PQ | 39,65 | 165,00 | 0,00 | 28,55 | -39,65 | 39,65 | 2,59 | 0,00
192 | ABS_150_gas | PQ | 57,41 | 165,00 | 0,00 | 41,34 | -57,41 | 57,41 | 24,88 | 0,00
192 | ABS_150_hydro | PQ | 0,01 | 165,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
192 | ABS_150_solar | PQ | 8,04 | 165,00 | 0,00 | 5,79 | -8,04 | 8,04 | 0,00 | 0,00
194 | ADL_150_WindOn | PQ | 0,42 | 165,00 | 0,00 | 0,30 | -0,42 | 0,42 | 0,03 | 0,00
194 | ADL_150_gas | PQ | 8,68 | 165,00 | 0,00 | 6,25 | -8,68 | 8,68 | 3,76 | 0,00
194 | ADL_150_solar | PQ | 4,70 | 165,00 | 0,00 | 3,39 | -4,70 | 4,70 | 0,00 | 0,00
195 | AHA_220_WindOff | PQ | 444,40 | 232,00 | 0,00 | 400,00 | -444,40 | 444,40 | 52,68 | 0,00
196 | AND_150_WindOn | PQ | 12,24 | 165,00 | 0,00 | 8,82 | -12,24 | 12,24 | 0,80 | 0,00
196 | AND_150_gas | PQ | 3,35 | 165,00 | 0,00 | 2,41 | -3,35 | 3,35 | 1,45 | 0,00
196 | AND_150_solar | PQ | 3,83 | 165,00 | 0,00 | 2,76 | -3,83 | 3,83 | 0,00 | 0,00
200 | BBR_150_WindOn | PQ | 137,79 | 165,00 | 0,00 | 99,22 | -137,79 | 137,79 | 9,01 | 0,00
200 | BBR_150_gas | PQ | 57,89 | 165,00 | 0,00 | 41,69 | -57,89 | 57,89 | 25,09 | 0,00
200 | BBR_150_solar | PQ | 7,09 | 165,00 | 0,00 | 5,11 | -7,09 | 7,09 | 0,00 | 0,00
201 | BDK_150_WindOn | PQ | 68,46 | 165,00 | 0,00 | 49,30 | -68,46 | 68,46 | 4,48 | 0,00
201 | BDK_150_gas | PQ | 104,77 | 165,00 | 0,00 | 75,44 | -104,77 | 104,77 | 45,41 | 0,00
201 | BDK_150_hydro | PQ | 0,10 | 165,00 | 0,00 | 0,07 | -0,10 | 0,10 | 0,03 | 0,00
201 | BDK_150_solar | PQ | 9,70 | 165,00 | 0,00 | 6,98 | -9,70 | 9,70 | 0,00 | 0,00
202 | BDR_150_WindOn | PQ | 37,24 | 165,00 | 0,00 | 26,81 | -37,24 | 37,24 | 2,44 | 0,00
202 | BDR_150_gas | PQ | 13,38 | 165,00 | 0,00 | 9,64 | -13,38 | 13,38 | 5,80 | 0,00
202 | BDR_150_hydro | PQ | 1,20 | 165,00 | 0,00 | 0,86 | -1,20 | 1,20 | 0,42 | 0,00
202 | BDR_150_solar | PQ | 13,31 | 165,00 | 0,00 | 9,58 | -13,31 | 13,31 | 0,00 | 0,00
203 | BED_150_WindOn | PQ | 178,21 | 165,00 | 0,00 | 128,33 | -178,21 | 178,21 | 11,66 | 0,00
203 | BED_150_gas | PQ | 24,63 | 165,00 | 0,00 | 17,73 | -24,63 | 24,63 | 10,67 | 0,00
203 | BED_150_solar | PQ | 12,02 | 165,00 | 0,00 | 8,66 | -12,02 | 12,02 | 0,00 | 0,00
204 | BIL_150_WindOn | PQ | 170,60 | 165,00 | 0,00 | 122,84 | -170,60 | 170,60 | 11,16 | 0,00
204 | BIL_150_gas | PQ | 52,37 | 165,00 | 0,00 | 37,71 | -52,37 | 52,37 | 22,70 | 0,00
204 | BIL_150_solar | PQ | 17,81 | 165,00 | 0,00 | 12,82 | -17,81 | 17,81 | 0,00 | 0,00
206 | BJH_150_WindOn | PQ | 31,17 | 165,00 | 0,00 | 22,45 | -31,17 | 31,17 | 2,04 | 0,00
206 | BJH_150_gas | PQ | 168,08 | 165,00 | 0,00 | 121,03 | -168,08 | 168,08 | 72,85 | 0,00
206 | BJH_150_hydro | PQ | 0,17 | 165,00 | 0,00 | 0,12 | -0,17 | 0,17 | 0,06 | 0,00
206 | BJH_150_solar | PQ | 16,08 | 165,00 | 0,00 | 11,58 | -16,08 | 16,08 | 0,00 | 0,00
207 | DYB_150_WindOn | PQ | 39,65 | 165,00 | 0,00 | 28,55 | -39,65 | 39,65 | 2,59 | 0,00
207 | DYB_150_gas | PQ | 17,57 | 165,00 | 0,00 | 12,65 | -17,57 | 17,57 | 7,61 | 0,00
207 | DYB_150_solar | PQ | 3,09 | 165,00 | 0,00 | 2,22 | -3,09 | 3,09 | 0,00 | 0,00
209 | EDR_150_solar | PQ | 0,00 | 165,00 | 0,00 | 0,00 | -0,00 | 0,00 | 0,00 | 0,00
215 | EST_150_WindOn | PQ | 0,02 | 165,00 | 0,00 | 0,01 | -0,02 | 0,02 | 0,00 | 0,00
215 | EST_150_gas | PQ | 28,76 | 165,00 | 0,00 | 20,71 | -28,76 | 28,76 | 12,47 | 0,00
215 | EST_150_solar | PQ | 3,09 | 165,00 | 0,00 | 2,23 | -3,09 | 3,09 | 0,00 | 0,00
216 | FER_150_WindOn | PQ | 23,93 | 165,00 | 0,00 | 17,23 | -23,93 | 23,93 | 1,57 | 0,00
216 | FER_150_gas | PQ | 10,32 | 165,00 | 0,00 | 7,43 | -10,32 | 10,32 | 4,47 | 0,00
216 | FER_150_solar | PQ | 3,99 | 165,00 | 0,00 | 2,88 | -3,99 | 3,99 | 0,00 | 0,00
219 | s_FGD1 | PV | 200,00 | 15,75 | 0,00 | 0,00 | -100,00 | 200,00 | 0,00 | 0,01 | 221 | 1,04
220 | FGD_150_WindOff | PQ | 23,33 | 165,00 | 0,00 | 16,80 | -23,33 | 23,33 | 2,77 | 0,00
220 | FGD_150_WindOn | PQ | 40,52 | 165,00 | 0,00 | 29,18 | -40,52 | 40,52 | 2,65 | 0,00
220 | FGD_150_gas | PQ | 81,68 | 165,00 | 0,00 | 58,82 | -81,68 | 81,68 | 35,40 | 0,00
220 | FGD_150_hydro | PQ | 0,02 | 165,00 | 0,00 | 0,02 | -0,02 | 0,02 | 0,01 | 0,00
220 | FGD_150_other | PQ | 19,48 | 165,00 | 0,00 | 17,53 | -19,48 | 19,48 | 17,53 | 0,00
220 | FGD_150_solar | PQ | 10,21 | 165,00 | 0,00 | 7,35 | -10,21 | 10,21 | 0,00 | 0,00
226 | FRD_150_WindOn | PQ | 34,63 | 165,00 | 0,00 | 24,93 | -34,63 | 34,63 | 2,27 | 0,00
226 | FRD_150_gas | PQ | 12,79 | 165,00 | 0,00 | 9,21 | -12,79 | 12,79 | 5,55 | 0,00
226 | FRD_150_solar | PQ | 6,13 | 165,00 | 0,00 | 4,42 | -6,13 | 6,13 | 0,00 | 0,00
227 | FRT_150_WindOn | PQ | 12,26 | 165,00 | 0,00 | 8,83 | -12,26 | 12,26 | 0,80 | 0,00
229 | s_FYVB8 | PV | 45,53 | 10,50 | 0,00 | 35,00 | -18,70 | 36,40 | 17,65 | 1,76 | 232 | 1,04
230 | s_FYVB7.1 | PV | 176,57 | 21,00 | 59,00 | 150,00 | -46,99 | 90,36 | 75,43 | 0,00 | 232 | 1,04
231 | FVO_150_WindOn | PQ | 38,55 | 165,00 | 0,00 | 27,76 | -38,55 | 38,55 | 2,52 | 0,00
231 | FVO_150_gas | PQ | 25,31 | 165,00 | 0,00 | 18,22 | -25,31 | 25,31 | 10,97 | 0,00
231 | FVO_150_other | PQ | 28,68 | 165,00 | 0,00 | 25,81 | -28,68 | 28,68 | 25,81 | 0,00
231 | FVO_150_solar | PQ | 10,66 | 165,00 | 0,00 | 7,68 | -10,66 | 10,66 | 0,00 | 0,00
233 | GRP_150_WindOn | PQ | 38,33 | 165,00 | 0,00 | 27,60 | -38,33 | 38,33 | 2,51 | 0,00
233 | GRP_150_gas | PQ | 25,49 | 165,00 | 0,00 | 18,36 | -25,49 | 25,49 | 11,05 | 0,00
233 | GRP_150_hydro | PQ | 0,02 | 165,00 | 0,00 | 0,01 | -0,02 | 0,02 | 0,01 | 0,00
233 | GRP_150_solar | PQ | 12,53 | 165,00 | 0,00 | 9,02 | -12,53 | 12,53 | 0,00 | 0,00
234 | HASV150_WindOn | PQ | 11,08 | 165,00 | 0,00 | 7,98 | -11,08 | 11,08 | 0,72 | 0,00
234 | HASV150_gas | PQ | 13,46 | 165,00 | 0,00 | 9,70 | -13,46 | 13,46 | 5,84 | 0,00
234 | HASV150_solar | PQ | 9,93 | 165,00 | 0,00 | 7,15 | -9,93 | 9,93 | 0,00 | 0,00
235 | HAT_150_WindOn | PQ | 27,19 | 165,00 | 0,00 | 19,58 | -27,19 | 27,19 | 1,78 | 0,00
235 | HAT_150_gas | PQ | 58,99 | 165,00 | 0,00 | 42,48 | -58,99 | 58,99 | 25,57 | 0,00
235 | HAT_150_hydro | PQ | 0,56 | 165,00 | 0,00 | 0,40 | -0,56 | 0,56 | 0,19 | 0,00
235 | HAT_150_solar | PQ | 20,33 | 165,00 | 0,00 | 14,64 | -20,33 | 20,33 | 0,00 | 0,00
236 | HER_150_WindOn | PQ | 141,62 | 165,00 | 0,00 | 101,98 | -141,62 | 141,62 | 9,26 | 0,00
236 | HER_150_gas | PQ | 57,52 | 165,00 | 0,00 | 41,42 | -57,52 | 57,52 | 24,93 | 0,00
236 | HER_150_hydro | PQ | 0,01 | 165,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
236 | HER_150_solar | PQ | 16,44 | 165,00 | 0,00 | 11,84 | -16,44 | 16,44 | 0,00 | 0,00
237 | s_VKHM1 | PV | 111,67 | 11,50 | 18,00 | 89,00 | -11,17 | 44,67 | 44,75 | 0,00 | 236 | 0,99
238 | HNB_150_WindOn | PQ | 49,27 | 165,00 | 0,00 | 35,47 | -49,27 | 49,27 | 3,22 | 0,00
238 | HNB_150_gas | PQ | 10,75 | 165,00 | 0,00 | 7,74 | -10,75 | 10,75 | 4,66 | 0,00
238 | HNB_150_solar | PQ | 6,59 | 165,00 | 0,00 | 4,74 | -6,59 | 6,59 | 0,00 | 0,00
239 | HOD_150_WindOn | PQ | 62,47 | 165,00 | 0,00 | 44,99 | -62,47 | 62,47 | 4,09 | 0,00
239 | HOD_150_gas | PQ | 40,76 | 165,00 | 0,00 | 29,35 | -40,76 | 40,76 | 17,67 | 0,00
239 | HOD_150_solar | PQ | 7,19 | 165,00 | 0,00 | 5,18 | -7,19 | 7,19 | 0,00 | 0,00
240 | HRA_150_WindOff | PQ | 177,76 | 165,00 | 0,00 | 128,00 | -177,76 | 177,76 | 21,07 | 0,00
241 | HRB_150_WindOff | PQ | 232,53 | 165,00 | 0,00 | 167,44 | -232,53 | 232,53 | 27,56 | 0,00
242 | HRC_220 | PQ | 666,60 | 232,00 | 0,00 | 160,00 | -666,60 | 666,60 | 78,23 | 0,00
243 | HSKV150_gas | PQ | 1,70 | 165,00 | 0,00 | 1,22 | -1,70 | 1,70 | 0,74 | 0,00
243 | HSKV150_solar | PQ | 2,91 | 165,00 | 0,00 | 2,10 | -2,91 | 2,91 | 0,00 | 0,00
244 | HVO_150_WindOn | PQ | 63,05 | 165,00 | 0,00 | 45,40 | -63,05 | 63,05 | 4,12 | 0,00
244 | HVO_150_gas | PQ | 4,40 | 165,00 | 0,00 | 3,17 | -4,40 | 4,40 | 1,91 | 0,00
244 | HVO_150_solar | PQ | 2,40 | 165,00 | 0,00 | 1,73 | -2,40 | 2,40 | 0,00 | 0,00
245 | HVV_150_gas | PQ | 1,69 | 165,00 | 0,00 | 1,22 | -1,69 | 1,69 | 0,73 | 0,00
245 | HVV_150_solar | PQ | 0,37 | 165,00 | 0,00 | 0,27 | -0,37 | 0,37 | 0,00 | 0,00
246 | HØN_150_WindOn | PQ | 10,20 | 165,00 | 0,00 | 7,35 | -10,20 | 10,20 | 0,67 | 0,00
246 | HØN_150_gas | PQ | 5,88 | 165,00 | 0,00 | 4,23 | -5,88 | 5,88 | 2,55 | 0,00
246 | HØN_150_solar | PQ | 6,17 | 165,00 | 0,00 | 4,44 | -6,17 | 6,17 | 0,00 | 0,00
247 | IDU_150_WindOn | PQ | 126,11 | 165,00 | 0,00 | 90,81 | -126,11 | 126,11 | 8,25 | 0,00
247 | IDU_150_gas | PQ | 9,09 | 165,00 | 0,00 | 6,54 | -9,09 | 9,09 | 3,94 | 0,00
247 | IDU_150_hydro | PQ | 0,56 | 165,00 | 0,00 | 0,40 | -0,56 | 0,56 | 0,19 | 0,00
247 | IDU_150_other | PQ | 33,46 | 165,00 | 0,00 | 30,12 | -33,46 | 33,46 | 30,12 | 0,00
247 | IDU_150_solar | PQ | 8,26 | 165,00 | 0,00 | 5,95 | -8,26 | 8,26 | 0,00 | 0,00
249 | KAE_150_WindOn | PQ | 95,20 | 165,00 | 0,00 | 68,55 | -95,20 | 95,20 | 6,23 | 0,00
249 | KAE_150_gas | PQ | 41,83 | 165,00 | 0,00 | 30,12 | -41,83 | 41,83 | 18,13 | 0,00
249 | KAE_150_hydro | PQ | 1,78 | 165,00 | 0,00 | 1,28 | -1,78 | 1,78 | 0,62 | 0,00
249 | KAE_150_solar | PQ | 10,52 | 165,00 | 0,00 | 7,58 | -10,52 | 10,52 | 0,00 | 0,00
254 | KBBV150_WindOn | PQ | 92,89 | 165,00 | 0,00 | 66,89 | -92,89 | 92,89 | 6,08 | 0,00
254 | KBBV150_gas | PQ | 36,08 | 165,00 | 0,00 | 25,98 | -36,08 | 36,08 | 15,64 | 0,00
254 | KBBV150_solar | PQ | 5,88 | 165,00 | 0,00 | 4,24 | -5,88 | 5,88 | 0,00 | 0,00
257 | KLF_150_WindOn | PQ | 85,13 | 165,00 | 0,00 | 61,30 | -85,13 | 85,13 | 5,57 | 0,00
257 | KLF_150_solar | PQ | 0,65 | 165,00 | 0,00 | 0,46 | -0,65 | 0,65 | 0,00 | 0,00
259 | KNA_150_WindOn | PQ | 33,48 | 165,00 | 0,00 | 24,11 | -33,48 | 33,48 | 2,19 | 0,00
259 | KNA_150_gas | PQ | 17,88 | 165,00 | 0,00 | 12,88 | -17,88 | 17,88 | 7,75 | 0,00
259 | KNA_150_hydro | PQ | 0,18 | 165,00 | 0,00 | 0,13 | -0,18 | 0,18 | 0,06 | 0,00
259 | KNA_150_solar | PQ | 17,65 | 165,00 | 0,00 | 12,71 | -17,65 | 17,65 | 0,00 | 0,00
260 | LAG_150_solar | PQ | 0,01 | 165,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
263 | LKR_150_WindOff | PQ | 111,10 | 165,00 | 0,00 | 100,00 | -111,10 | 111,10 | 13,17 | 0,00
263 | LKR_150_WindOn | PQ | 210,20 | 165,00 | 0,00 | 151,36 | -210,20 | 210,20 | 13,75 | 0,00
263 | LKR_150_gas | PQ | 26,53 | 165,00 | 0,00 | 19,11 | -26,53 | 26,53 | 11,50 | 0,00
263 | LKR_150_solar | PQ | 5,96 | 165,00 | 0,00 | 4,29 | -5,96 | 5,96 | 0,00 | 0,00
264 | LOL_150_WindOn | PQ | 18,16 | 165,00 | 0,00 | 13,08 | -18,16 | 18,16 | 1,19 | 0,00
264 | LOL_150_gas | PQ | 74,23 | 165,00 | 0,00 | 53,45 | -74,23 | 74,23 | 32,17 | 0,00
264 | LOL_150_hydro | PQ | 0,02 | 165,00 | 0,00 | 0,02 | -0,02 | 0,02 | 0,01 | 0,00
264 | LOL_150_solar | PQ | 6,46 | 165,00 | 0,00 | 4,66 | -6,46 | 6,46 | 0,00 | 0,00
265 | LYK_150_WindOn | PQ | 47,83 | 165,00 | 0,00 | 34,44 | -47,83 | 47,83 | 3,13 | 0,00
265 | LYK_150_gas | PQ | 19,06 | 165,00 | 0,00 | 13,72 | -19,06 | 19,06 | 8,26 | 0,00
265 | LYK_150_other | PQ | 22,21 | 165,00 | 0,00 | 19,99 | -22,21 | 22,21 | 19,99 | 0,00
265 | LYK_150_solar | PQ | 5,12 | 165,00 | 0,00 | 3,69 | -5,12 | 5,12 | 0,00 | 0,00
266 | MAG_150_WindOn | PQ | 46,86 | 165,00 | 0,00 | 33,74 | -46,86 | 46,86 | 3,07 | 0,00
266 | MAG_150_gas | PQ | 46,84 | 165,00 | 0,00 | 33,73 | -46,84 | 46,84 | 20,30 | 0,00
266 | MAG_150_hydro | PQ | 0,33 | 165,00 | 0,00 | 0,24 | -0,33 | 0,33 | 0,12 | 0,00
266 | MAG_150_solar | PQ | 11,95 | 165,00 | 0,00 | 8,60 | -11,95 | 11,95 | 0,00 | 0,00
267 | MAL_150_WindOff | PQ | 31,11 | 165,00 | 0,00 | 22,40 | -31,11 | 31,11 | 3,69 | 0,00
267 | MAL_150_WindOn | PQ | 13,53 | 165,00 | 0,00 | 9,75 | -13,53 | 13,53 | 0,89 | 0,00
267 | MAL_150_gas | PQ | 5,97 | 165,00 | 0,00 | 4,30 | -5,97 | 5,97 | 2,59 | 0,00
267 | MAL_150_solar | PQ | 8,63 | 165,00 | 0,00 | 6,21 | -8,63 | 8,63 | 0,00 | 0,00
269 | MES_150_WindOn | PQ | 68,70 | 165,00 | 0,00 | 49,47 | -68,70 | 68,70 | 4,49 | 0,00
269 | MES_150_gas | PQ | 7,34 | 165,00 | 0,00 | 5,29 | -7,34 | 7,34 | 3,18 | 0,00
269 | MES_150_solar | PQ | 10,72 | 165,00 | 0,00 | 7,72 | -10,72 | 10,72 | 0,00 | 0,00
270 | s_SSVB3 | PV | 458,82 | 19,00 | 35,00 | 390,00 | -72,83 | 239,29 | 258,00 | 0,00 | 272 | 0,99
272 | MKS_150_OCGTOld | PQ | 15,55 | 165,00 | 0,00 | 11,20 | -15,55 | 15,55 | 0,00 | 0,00
274 | MLP_150_WindOn | PQ | 22,28 | 165,00 | 0,00 | 16,04 | -22,28 | 22,28 | 1,46 | 0,00
274 | MLP_150_gas | PQ | 5,67 | 165,00 | 0,00 | 4,09 | -5,67 | 5,67 | 2,46 | 0,00
274 | MLP_150_other | PQ | 23,06 | 165,00 | 0,00 | 20,76 | -23,06 | 23,06 | 20,76 | 0,00
274 | MLP_150_solar | PQ | 12,06 | 165,00 | 0,00 | 8,68 | -12,06 | 12,06 | 0,00 | 0,00
275 | MLU_150_WindOn | PQ | 34,72 | 165,00 | 0,00 | 25,00 | -34,72 | 34,72 | 2,27 | 0,00
275 | MLU_150_gas | PQ | 67,80 | 165,00 | 0,00 | 48,82 | -67,80 | 67,80 | 29,38 | 0,00
275 | MLU_150_solar | PQ | 6,67 | 165,00 | 0,00 | 4,80 | -6,67 | 6,67 | 0,00 | 0,00
276 | MOSV150_WindOn | PQ | 50,45 | 165,00 | 0,00 | 36,33 | -50,45 | 50,45 | 3,30 | 0,00
276 | MOSV150_gas | PQ | 21,09 | 165,00 | 0,00 | 15,19 | -21,09 | 21,09 | 9,14 | 0,00
276 | MOSV150_solar | PQ | 5,45 | 165,00 | 0,00 | 3,93 | -5,45 | 5,45 | 0,00 | 0,00
277 | NOR_150_WindOn | PQ | 62,08 | 165,00 | 0,00 | 44,70 | -62,08 | 62,08 | 4,06 | 0,00
277 | NOR_150_gas | PQ | 23,33 | 165,00 | 0,00 | 16,80 | -23,33 | 23,33 | 10,11 | 0,00
277 | NOR_150_solar | PQ | 6,17 | 165,00 | 0,00 | 4,44 | -6,17 | 6,17 | 0,00 | 0,00
278 | NSP_150_WindOn | PQ | 75,86 | 165,00 | 0,00 | 54,62 | -75,86 | 75,86 | 4,96 | 0,00
278 | NSP_150_gas | PQ | 54,51 | 165,00 | 0,00 | 39,25 | -54,51 | 54,51 | 23,62 | 0,00
278 | NSP_150_solar | PQ | 9,38 | 165,00 | 0,00 | 6,76 | -9,38 | 9,38 | 0,00 | 0,00
279 | s_NJVB3 | PV | 523,80 | 21,00 | 82,00 | 440,00 | -135,00 | 290,00 | 410,00 | 0,00 | 282 | 1,04
281 | NVV_150_OCGTOld | PQ | 27,77 | 165,00 | 0,00 | 20,00 | -27,77 | 27,77 | 0,00 | 0,00
281 | NVV_150_WindOn | PQ | 13,33 | 165,00 | 0,00 | 9,60 | -13,33 | 13,33 | 0,87 | 0,00
283 | OSØ_150_solar | PQ | 0,47 | 165,00 | 0,00 | 0,34 | -0,47 | 0,47 | 0,00 | 0,00
285 | RAM_150_WindOff | PQ | 130,21 | 165,00 | 0,00 | 13,76 | -130,21 | 130,21 | 15,44 | 0,00
285 | RAM_150_WindOn | PQ | 134,77 | 165,00 | 0,00 | 97,04 | -134,77 | 134,77 | 8,82 | 0,00
285 | RAM_150_gas | PQ | 1,81 | 165,00 | 0,00 | 1,30 | -1,81 | 1,81 | 0,78 | 0,00
285 | RAM_150_solar | PQ | 2,55 | 165,00 | 0,00 | 1,84 | -2,55 | 2,55 | 0,00 | 0,00
287 | RIB_150_WindOn | PQ | 38,37 | 165,00 | 0,00 | 27,63 | -38,37 | 38,37 | 2,51 | 0,00
287 | RIB_150_gas | PQ | 21,43 | 165,00 | 0,00 | 15,43 | -21,43 | 21,43 | 9,29 | 0,00
287 | RIB_150_hydro | PQ | 0,12 | 165,00 | 0,00 | 0,09 | -0,12 | 0,12 | 0,04 | 0,00
287 | RIB_150_solar | PQ | 5,20 | 165,00 | 0,00 | 3,75 | -5,20 | 5,20 | 0,00 | 0,00
289 | RYT_150_WindOn | PQ | 2,86 | 165,00 | 0,00 | 2,06 | -2,86 | 2,86 | 0,19 | 0,00
289 | RYT_150_gas | PQ | 37,13 | 165,00 | 0,00 | 26,74 | -37,13 | 37,13 | 16,09 | 0,00
289 | RYT_150_solar | PQ | 7,10 | 165,00 | 0,00 | 5,11 | -7,10 | 7,10 | 0,00 | 0,00
290 | SBA_150_WindOff | PQ | 11,78 | 165,00 | 0,00 | 8,48 | -11,78 | 11,78 | 1,40 | 0,00
290 | SBA_150_WindOn | PQ | 17,34 | 165,00 | 0,00 | 12,48 | -17,34 | 17,34 | 1,13 | 0,00
290 | SBA_150_gas | PQ | 52,62 | 165,00 | 0,00 | 37,89 | -52,62 | 52,62 | 22,81 | 0,00
290 | SBA_150_hydro | PQ | 0,03 | 165,00 | 0,00 | 0,02 | -0,03 | 0,03 | 0,01 | 0,00
290 | SBA_150_solar | PQ | 5,02 | 165,00 | 0,00 | 3,62 | -5,02 | 5,02 | 0,00 | 0,00
291 | SFE_150_WindOn | PQ | 2,51 | 165,00 | 0,00 | 1,81 | -2,51 | 2,51 | 0,16 | 0,00
291 | SFE_150_solar | PQ | 0,40 | 165,00 | 0,00 | 0,29 | -0,40 | 0,40 | 0,00 | 0,00
294 | SHE_150_WindOn | PQ | 142,46 | 165,00 | 0,00 | 102,58 | -142,46 | 142,46 | 9,32 | 0,00
294 | SHE_150_gas | PQ | 55,96 | 165,00 | 0,00 | 40,30 | -55,96 | 55,96 | 24,26 | 0,00
294 | SHE_150_hydro | PQ | 0,05 | 165,00 | 0,00 | 0,03 | -0,05 | 0,05 | 0,02 | 0,00
294 | SHE_150_solar | PQ | 25,58 | 165,00 | 0,00 | 18,42 | -25,58 | 25,58 | 0,00 | 0,00
296 | SKA_150_WindOn | PQ | 0,01 | 165,00 | 0,00 | 0,01 | -0,01 | 0,01 | 0,00 | 0,00
296 | SKA_150_solar | PQ | 1,40 | 165,00 | 0,00 | 1,01 | -1,40 | 1,40 | 0,00 | 0,00
297 | STR_150_WindOn | PQ | 38,73 | 165,00 | 0,00 | 27,89 | -38,73 | 38,73 | 2,53 | 0,00
297 | STR_150_gas | PQ | 37,11 | 165,00 | 0,00 | 26,72 | -37,11 | 37,11 | 16,08 | 0,00
297 | STR_150_solar | PQ | 6,30 | 165,00 | 0,00 | 4,54 | -6,30 | 6,30 | 0,00 | 0,00
298 | STSV150_WindOn | PQ | 153,75 | 165,00 | 0,00 | 110,71 | -153,75 | 153,75 | 10,06 | 0,00
298 | STSV150_gas | PQ | 23,02 | 165,00 | 0,00 | 16,58 | -23,02 | 23,02 | 9,98 | 0,00
298 | STSV150_solar | PQ | 8,95 | 165,00 | 0,00 | 6,45 | -8,95 | 8,95 | 0,00 | 0,00
299 | SVB_150_WindOn | PQ | 94,64 | 165,00 | 0,00 | 68,14 | -94,64 | 94,64 | 6,19 | 0,00
299 | SVB_150_gas | PQ | 32,69 | 165,00 | 0,00 | 23,54 | -32,69 | 32,69 | 14,17 | 0,00
299 | SVB_150_solar | PQ | 15,05 | 165,00 | 0,00 | 10,84 | -15,05 | 15,05 | 0,00 | 0,00
300 | s_SKVB3 | PV | 511,91 | 21,00 | 59,00 | 370,00 | -107,50 | 322,51 | 0,00 | 0,00 | 303 | 1,04
300 | s_SKVB3.1 | PV | 71,43 | 21,00 | 0,00 | 60,00 | -15,00 | 45,00 | 30,17 | 0,00 | 303 | 1,04
302 | SVS_150_gas | PQ | 2,22 | 165,00 | 0,00 | 1,60 | -2,22 | 2,22 | 0,96 | 0,00
304 | SØN_150_WindOn | PQ | 27,08 | 165,00 | 0,00 | 19,50 | -27,08 | 27,08 | 1,77 | 0,00
304 | SØN_150_gas | PQ | 98,55 | 165,00 | 0,00 | 70,96 | -98,55 | 98,55 | 42,71 | 0,00
304 | SØN_150_solar | PQ | 10,19 | 165,00 | 0,00 | 7,34 | -10,19 | 10,19 | 0,00 | 0,00
305 | TAN_150_WindOn | PQ | 39,25 | 165,00 | 0,00 | 28,26 | -39,25 | 39,25 | 2,57 | 0,00
305 | TAN_150_gas | PQ | 23,51 | 165,00 | 0,00 | 16,93 | -23,51 | 23,51 | 10,19 | 0,00
305 | TAN_150_hydro | PQ | 5,84 | 165,00 | 0,00 | 4,21 | -5,84 | 5,84 | 2,05 | 0,00
305 | TAN_150_solar | PQ | 7,71 | 165,00 | 0,00 | 5,55 | -7,71 | 7,71 | 0,00 | 0,00
306 | THY_150_WindOn | PQ | 69,51 | 165,00 | 0,00 | 50,05 | -69,51 | 69,51 | 4,55 | 0,00
306 | THY_150_gas | PQ | 18,29 | 165,00 | 0,00 | 13,17 | -18,29 | 18,29 | 7,93 | 0,00
306 | THY_150_hydro | PQ | 0,24 | 165,00 | 0,00 | 0,18 | -0,24 | 0,24 | 0,09 | 0,00
306 | THY_150_solar | PQ | 8,74 | 165,00 | 0,00 | 6,30 | -8,74 | 8,74 | 0,00 | 0,00
307 | THØ_150_WindOn | PQ | 75,00 | 165,00 | 0,00 | 54,01 | -75,00 | 75,00 | 4,91 | 0,00
307 | THØ_150_gas | PQ | 17,47 | 165,00 | 0,00 | 12,58 | -17,47 | 17,47 | 7,57 | 0,00
307 | THØ_150_solar | PQ | 6,68 | 165,00 | 0,00 | 4,81 | -6,68 | 6,68 | 0,00 | 0,00
310 | s_TJE1 | PV | 160,00 | 13,00 | 0,00 | 0,00 | -120,00 | 160,00 | 0,00 | 0,00 | 312 | 0,99
311 | TJE_150_solar | PQ | 0,01 | 165,00 | 0,00 | 0,00 | -0,01 | 0,01 | 0,00 | 0,00
325 | s_VHA1 | PV | 100,00 | 12,00 | 0,00 | 0,00 | -50,00 | 105,00 | 0,00 | 0,00 | 326 | 0,99
326 | VHA_150_WindOn | PQ | 50,39 | 165,00 | 0,00 | 36,29 | -50,39 | 50,39 | 3,30 | 0,00
326 | VHA_150_gas | PQ | 18,32 | 165,00 | 0,00 | 13,19 | -18,32 | 18,32 | 7,94 | 0,00
326 | VHA_150_solar | PQ | 4,28 | 165,00 | 0,00 | 3,08 | -4,28 | 4,28 | 0,00 | 0,00
335 | VID_150_WindOn | PQ | 94,26 | 165,00 | 0,00 | 67,88 | -94,26 | 94,26 | 6,17 | 0,00
335 | VID_150_gas | PQ | 27,30 | 165,00 | 0,00 | 19,66 | -27,30 | 27,30 | 11,83 | 0,00
335 | VID_150_hydro | PQ | 0,00 | 165,00 | 0,00 | 0,00 | -0,00 | 0,00 | 0,00 | 0,00
335 | VID_150_solar | PQ | 9,47 | 165,00 | 0,00 | 6,82 | -9,47 | 9,47 | 0,00 | 0,00
336 | VIL_150_WindOn | PQ | 92,50 | 165,00 | 0,00 | 66,61 | -92,50 | 92,50 | 6,05 | 0,00
336 | VIL_150_gas | PQ | 21,39 | 165,00 | 0,00 | 15,40 | -21,39 | 21,39 | 9,27 | 0,00
336 | VIL_150_solar | PQ | 5,71 | 165,00 | 0,00 | 4,11 | -5,71 | 5,71 | 0,00 | 0,00
337 | s_ESVB3 | SL | 528,00 | 19,00 | 70,00 | 402,00 | -155,00 | 245,00 | 40,20 | 0,00 | 265 | 0,99
339 | ÅBØ_150_other | PQ | 29,76 | 165,00 | 0,00 | 26,78 | -29,76 | 29,76 | 26,78 | 0,00
339 | ÅBØ_150_solar | PQ | 0,63 | 165,00 | 0,00 | 0,45 | -0,63 | 0,63 | 0,00 | 0,00
340 | ÅSP_150_WindOn | PQ | 17,64 | 165,00 | 0,00 | 12,70 | -17,64 | 17,64 | 1,15 | 0,00
340 | ÅSP_150_gas | PQ | 46,66 | 165,00 | 0,00 | 33,60 | -46,66 | 46,66 | 20,22 | 0,00
340 | ÅSP_150_solar | PQ | 3,01 | 165,00 | 0,00 | 2,17 | -3,01 | 3,01 | 0,00 | 0,00

## Load
Load Data | Energinet.dk | 2020
Load Index | Load Name | Area Name | Act.P[MW] | Act.Q[Mvar]
0 | l_MRP_132_S1_SE | SVERIGE | -150,0 | 0,0
1 | l_MRP_132_S2_SE | SVERIGE | -150,0 | 0,0
2 | l_SÅN_400_S1_SE | SVERIGE | -500,0 | 0,0
3 | l_SÅN_400_S2_SE | SVERIGE | -500,0 | 0,0
0 | MRP1 | SVERIGE | 0,0 | 0,0
1 | MRP2 | SVERIGE | 0,0 | 0,0
2 | SÅN1 | SVERIGE | 0,0 | 0,0
5 | l_BWT_400 | TYSKLAND | 0,0 | 0,0
9 | l_UCTE_400 | TYSKLAND | 235,0 | 0,0
21 | l_UWN_150 | FLENSBORG | 74,8 | 25,8
53 | l_ALL_132 | ENDKE | 58,0 | 16,3
54 | l_AMF_132 | ENDKE | -0,0 | 0,0
55 | l_AMK_132 | ENDKE | 71,6 | 21,9
58 | l_AMV_132 | ENDKE | 52,9 | 14,7
61 | l_ASV_132 | ENDKE | 0,0 | 0,0
71 | l_BAG_132 | ENDKE | 22,3 | 7,8
72 | l_BAL_132 | ENDKE | 12,4 | 3,8
73 | l_BEL_132 | ENDKE | 53,7 | 15,5
82 | l_BLA_132 | ENDKE | 52,0 | 15,5
83 | l_BOR_132 | ENDKE | 50,5 | 6,8
84 | l_BRY_132 | ENDKE | 74,7 | 18,1
85 | l_DDS_132 | ENDKE | 0,0 | 0,2
86 | l_DDS_132-1 | ENDKE | 0,0 | 0,0
87 | l_DYR_132 | ENDKE | 22,1 | 7,7
88 | l_EBY_132 | ENDKE | 71,2 | 24,1
89 | l_ESK_132 | ENDKE | 22,8 | 7,8
91 | l_FLA_132 | ENDKE | 25,3 | 8,3
92 | l_FNM_132 | ENDKE | 9,5 | 2,9
95 | l_GLN_132 | ENDKE | 129,4 | 31,1
97 | l_GRN_132 | ENDKE | 22,3 | 7,8
101 | l_HASØ132 | ENDKE | 30,5 | 8,4
102 | l_HCV_132 | ENDKE | 101,1 | 38,9
104 | l_HDE_132 | ENDKE | 27,5 | 12,2
105 | l_HEJ_132 | ENDKE | 60,6 | -4,1
113 | l_HMA_132 | ENDKE | 4,9 | 1,4
114 | l_HSKØ132 | ENDKE | 18,9 | 6,4
115 | l_HSTØ132 | ENDKE | 13,9 | 4,3
118 | l_IDE_132 | ENDKE | 19,6 | 5,3
123 | l_JER_132 | ENDKE | 40,9 | 17,8
124 | l_KAK_132 | ENDKE | 13,3 | 4,4
125 | l_KAM_132 | ENDKE | 25,5 | 7,1
126 | l_KARA132 | ENDKE | -0,0 | -0,0
127 | l_KBG_132 | ENDKE | 26,6 | 7,4
128 | l_KBG_132-1 | ENDKE | 0,0 | 0,0
129 | l_KFA_220 | ENDKE | 0,0 | 0,0
130 | l_KFB_220 | ENDKE | 0,0 | 0,0
135 | l_KRL_132 | ENDKE | 6,4 | 2,0
136 | l_KSV_132 | ENDKE | 6,3 | 1,8
147 | l_LIN_132 | ENDKE | 54,0 | -1,5
148 | l_LUP_132 | ENDKE | 8,6 | 2,8
149 | l_MAV_132 | ENDKE | 0,8 | 0,3
150 | l_MOSØ132 | ENDKE | 20,2 | 6,8
151 | l_MÅLØ132 | ENDKE | 23,6 | 8,4
152 | l_NAM_132 | ENDKE | 35,2 | 11,7
153 | l_NSV_132 | ENDKE | 24,3 | 3,0
154 | l_NVS_132 | ENDKE | 27,7 | 7,5
155 | l_NYM_132 | ENDKE | 6,8 | 2,1
156 | l_NYM_132-1 | ENDKE | 0,0 | 0,0
157 | l_NYR_132 | ENDKE | 28,7 | 7,8
158 | l_ORH_132 | ENDKE | 2,2 | 0,6
159 | l_OST_132 | ENDKE | 9,0 | 2,6
161 | l_RAD_132 | ENDKE | 24,3 | 6,0
162 | l_RBY_132 | ENDKE | 13,6 | 4,7
163 | l_RDB_132 | ENDKE | 0,0 | 0,0
164 | l_RDS_132 | ENDKE | 0,0 | 0,0
166 | l_RIN_132 | ENDKE | 28,3 | 3,4
167 | l_SIB_132 | ENDKE | 11,0 | 3,8
168 | l_SKLØ132 | ENDKE | 11,3 | 1,6
169 | l_SMK_132 | ENDKE | 86,6 | 31,9
171 | l_SPA_132 | ENDKE | 26,5 | 7,0
172 | l_SPR_132 | ENDKE | 11,9 | 3,6
173 | l_STA_132 | ENDKE | 88,1 | 19,2
174 | l_STSØ132 | ENDKE | 9,9 | 3,1
176 | l_STV_132 | ENDKE | 26,6 | 9,4
177 | l_TEG_132 | ENDKE | 63,2 | 10,6
179 | l_TOR_132 | ENDKE | 35,7 | 10,0
180 | l_VAL_132 | ENDKE | 57,4 | 7,2
182 | l_VEJ_132 | ENDKE | 56,9 | 13,4
183 | l_VIK_132 | ENDKE | 53,0 | 15,1
185 | l_VLO_132 | ENDKE | 25,0 | -1,2
186 | l_VSA_132 | ENDKE | 0,0 | 0,1
187 | l_ØLS_132 | ENDKE | 33,7 | 8,6
188 | l_ØSH_132 | ENDKE | 21,1 | 4,2
192 | l_ABS_150 | ENDKW | 33,9 | 3,5
194 | l_ADL_150 | ENDKW | 44,7 | 3,0
196 | l_AND_150 | ENDKW | 33,9 | -1,1
200 | l_BBR_150 | ENDKW | 44,8 | 4,5
201 | l_BDK_150 | ENDKW | 54,2 | -12,7
202 | l_BDR_150 | ENDKW | 72,5 | 7,5
203 | l_BED_150 | ENDKW | 23,3 | -12,9
204 | l_BIL_150 | ENDKW | 45,7 | -18,3
206 | l_BJH_150 | ENDKW | 71,6 | -3,5
207 | l_DYB_150 | ENDKW | 24,1 | -10,8
215 | l_EST_150 | ENDKW | 29,1 | 2,8
216 | l_FER_150 | ENDKW | 26,5 | -2,7
220 | l_FGD_150 | ENDKW | 69,9 | 17,8
226 | l_FRD_150 | ENDKW | 18,7 | 3,9
227 | l_FRT_150 | ENDKW | 0,0 | 0,0
231 | l_FVO_150 | ENDKW | 91,4 | 0,5
233 | l_GRP_150 | ENDKW | 43,5 | -1,7
234 | l_HASV150 | ENDKW | 88,5 | 6,8
235 | l_HAT_150 | ENDKW | 117,7 | 23,4
236 | l_HER_150 | ENDKW | 99,2 | 1,1
238 | l_HNB_150 | ENDKW | 22,3 | -8,3
239 | l_HOD_150 | ENDKW | 46,6 | 5,5
243 | l_HSKV150 | ENDKW | 55,3 | 9,4
244 | l_HVO_150 | ENDKW | 11,8 | -2,2
245 | l_HVV_150 | ENDKW | 26,2 | 3,6
246 | l_HØN_150 | ENDKW | 36,0 | 6,4
247 | l_IDU_150 | ENDKW | 65,9 | 15,0
249 | l_KAE_150 | ENDKW | 57,3 | 3,0
254 | l_KBBV150 | ENDKW | 33,5 | -7,8
257 | l_KLF_150 | ENDKW | 3,4 | -3,0
259 | l_KNA_150 | ENDKW | 71,4 | 1,9
263 | l_LKR_150 | ENDKW | 22,2 | 0,8
264 | l_LOL_150 | ENDKW | 39,0 | -3,1
265 | l_LYK_150 | ENDKW | 52,5 | 5,6
266 | l_MAG_150 | ENDKW | 52,8 | -10,3
267 | l_MAL_150 | ENDKW | 44,5 | 4,6
269 | l_MES_150 | ENDKW | 57,4 | -8,5
272 | l_MKS_150 | ENDKW | 61,5 | 2,9
274 | l_MLP_150 | ENDKW | 65,6 | 7,8
275 | l_MLU_150 | ENDKW | 55,8 | 3,3
276 | l_MOSV150 | ENDKW | 29,8 | -9,1
277 | l_NOR_150 | ENDKW | 32,9 | -12,4
278 | l_NSP_150 | ENDKW | 38,9 | -4,1
281 | l_NVV_150 | ENDKW | 0,0 | 0,1
283 | l_OSØ_150 | ENDKW | 26,7 | 0,2
284 | l_OVE_150 | ENDKW | 56,2 | 17,6
285 | l_RAM_150 | ENDKW | 11,2 | -1,7
287 | l_RIB_150 | ENDKW | 28,3 | -4,3
288 | l_RSL_150 | ENDKW | 15,7 | 4,2
289 | l_RYT_150 | ENDKW | 71,3 | 6,7
290 | l_SBA_150 | ENDKW | 47,1 | -14,8
291 | l_SFE_150 | ENDKW | 3,4 | -1,3
294 | l_SHE_150 | ENDKW | 107,1 | -3,6
295 | l_SIN_150 | ENDKW | 23,3 | 6,5
296 | l_SKA_150 | ENDKW | 15,3 | 2,7
297 | l_STR_150 | ENDKW | 35,6 | 6,2
298 | l_STSV150 | ENDKW | 43,1 | -8,7
299 | l_SVB_150 | ENDKW | 59,1 | -5,4
304 | l_SØN_150 | ENDKW | 48,0 | 2,1
305 | l_TAN_150 | ENDKW | 45,8 | -0,9
306 | l_THY_150 | ENDKW | 35,4 | 3,1
307 | l_THØ_150 | ENDKW | 28,7 | -8,6
311 | l_TJE_150 | ENDKW | 0,0 | 0,0
326 | l_VHA_150 | ENDKW | 15,5 | -5,8
335 | l_VID_150 | ENDKW | 42,3 | 5,2
336 | l_VIL_150 | ENDKW | 25,6 | -14,9
339 | l_ÅBØ_150 | ENDKW | 35,7 | 6,7
340 | l_ÅSP_150 | ENDKW | 25,3 | -5,2

## Shunt
Shunt Data | Energinet.dk | 2020
Bus Index | Shunt Name | Shunt Type | Max.Step | Act.Step | L[Mvar] | C[Mvar] | Nominal Voltage[kV] | Switchable | Voltage min[pu] | Voltage max[pu] | Control Bus Index
78 | BJS_400-R41 | Shunt Reactor | 1 | 0 | 100,00 | 0,00 | 400 | Yes | 1,02 | 1,04 | 78
83 | BOR_132-R11 | Shunt Reactor | 1 | 1 | 60,00 | 0,00 | 132 | No
90 | FEM_132-R11 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 90
95 | GLN_132-R11 | Shunt Reactor | 18 | 9 | 5,80 | 0,00 | 132 | Yes | 0,98 | 1,04 | 95
100 | GØR_400-R41 | Shunt Reactor | 1 | 0 | 120,00 | 0,00 | 400 | Yes | 1,02 | 1,04 | 100
102 | HCV_132-R132 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 132 | Yes | 0,97 | 1,03 | 102
114 | HSKØ132-R11 | Shunt Reactor | 1 | 0 | 100,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 114
116 | HVE_132-R11 | Shunt Reactor | 1 | 0 | 63,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 116
116 | HVE_132-R13 | Shunt Reactor | 1 | 0 | 63,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 116
117 | HDE_400-ZL44 | Shunt Reactor | 25 | 13 | 5,60 | 0,00 | 400 | Yes | 1,01 | 1,04 | 117
117 | HKS_400-R45 | Shunt Reactor | 25 | 13 | 5,60 | 0,00 | 400 | Yes | 1,01 | 1,04 | 117
117 | HKS_400-R46 | Shunt Reactor | 25 | 13 | 5,60 | 0,00 | 400 | Yes | 1,01 | 1,04 | 117
117 | HVE_400-R41 | Shunt Reactor | 1 | 1 | 100,00 | 0,00 | 400 | Yes | 1,02 | 1,04 | 117
120 | ISH_132-KON | Shunt Capacitor | 1 | 0 | 0,00 | 100,00 | 138 | Yes | 0,98 | 1,05 | 120
120 | ISH_132-R11 | Shunt Reactor | 1 | 1 | 50,01 | 0,00 | 132 | No
129 | KFA_220-ZL1 | Shunt Reactor | 1 | 1 | 120,00 | 0,00 | 235 | No
149 | MAV_132-R11 | Shunt Reactor | 1 | 0 | 40,12 | 0,00 | 132 | Yes | 0,98 | 1,05 | 149
159 | OST_132-R11 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 132 | No
160 | RAD_009-KON | Shunt Capacitor | 1 | 1 | 0,00 | 106,60 | 10 | No
161 | RAD_132-R12 | Shunt Reactor | 1 | 1 | 50,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 161
162 | RBY_132-R11 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 162
176 | STV_132-R11 | Shunt Reactor | 1 | 1 | 60,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 176
178 | TOL_220-ZL1 | Shunt Reactor | 1 | 1 | 120,00 | 0,00 | 235 | No
178 | TOL_220-ZL2 | Shunt Reactor | 25 | 13 | 4,80 | 0,00 | 235 | Yes | 0,95 | 1,04 | 178
178 | TOL_220-ZL3 | Shunt Reactor | 25 | 13 | 4,80 | 0,00 | 235 | Yes | 0,95 | 1,04 | 178
178 | TOL_220-ZL4 | Shunt Reactor | 1 | 1 | 60,00 | 0,00 | 235 | Yes | 0,95 | 1,04 | 178
182 | VEJ_132-R11 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 132 | Yes | 0,98 | 1,05 | 182
192 | ABS_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 192
198 | ASR_400-ZL2 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 198
199 | ASR_400_REVZL | Shunt Reactor | 29 | 15 | 3,79 | 0,00 | 400 | Yes | 1,01 | 1,04 | 199
200 | BBR_150-ZL1 | Shunt Reactor | 1 | 1 | 50,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 200
201 | BDK_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 201
202 | BDR_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 202
203 | BED_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 203
203 | BED_150-ZL2 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 203
204 | BIL_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 170 | Yes | 0,97 | 1,01 | 204
204 | BIL_150-ZL2 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 204
206 | BJH_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 170 | Yes | 0,97 | 1,01 | 206
206 | BJH_150-ZL2 | Shunt Reactor | 1 | 1 | 50,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 206
209 | EDR_150-ZL1 | Shunt Reactor | 1 | 1 | 80,97 | 0,00 | 170 | Yes | 0,97 | 1,01 | 209
210 | EDR_150-ZL2 | Shunt Reactor | 1 | 0 | 80,00 | 0,00 | 170 | Yes | 0,88 | 1,03 | 210
210 | EDR_150-ZL3 | Shunt Reactor | 1 | 0 | 40,00 | 0,00 | 170 | Yes | 0,88 | 1,03 | 210
211 | EDR_220-ZL1 | Shunt Reactor | 25 | 14 | 4,80 | 0,00 | 235 | Yes | 1,01 | 1,04 | 214
211 | EDR_220-ZL2 | Shunt Reactor | 25 | 14 | 4,80 | 0,00 | 235 | Yes | 1,01 | 1,04 | 214
214 | EDR_400_ZL1 | Shunt Reactor | 29 | 15 | 3,79 | 0,00 | 420 | Yes | 1,01 | 1,04 | 214
216 | FER_150-ZL31- | Shunt Reactor | 1 | 1 | 80,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 216
216 | FER_150-ZL32 | Shunt Reactor | 1 | 0 | 40,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 216
217 | FER_400-ZL1 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 217
217 | FER_400-ZL2 | Shunt Reactor | 1 | 0 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 217
220 | FGD_150-ZL1 | Shunt Reactor | 1 | 1 | 80,68 | 0,00 | 170 | Yes | 0,97 | 1,01 | 220
221 | FGD_400-ZL1 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 221
227 | FRT_150-ZL31 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,98 | 1,01 | 227
231 | FVO_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 231
234 | HASV150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 234
243 | HSKV150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 243
247 | IDU_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 247
247 | IDU_150-ZL3 | Shunt Reactor | 1 | 1 | 65,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 247
248 | IDU_400-ZL1 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 248
249 | KAE_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 249
252 | KAS_150-ZL1 | Shunt Reactor | 1 | 1 | 168,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 252
253 | KAS_400-ZL1 | Shunt Reactor | 1 | 1 | 100,30 | 0,00 | 400 | Yes | 1,01 | 1,04 | 253
255 | KIN_150-ZL1- | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 170 | Yes | 0,97 | 1,01 | 255
257 | KLF_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 257
260 | LAG_150-ZL1 | Shunt Reactor | 1 | 1 | 50,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 260
261 | LAG_400-ZL1 | Shunt Reactor | 1 | 1 | 141,12 | 0,00 | 420 | Yes | 1,01 | 1,04 | 261
261 | LAG_400-ZL2 | Shunt Reactor | 29 | 15 | 3,79 | 0,00 | 400 | Yes | 1,01 | 1,04 | 261
263 | LKR_150-ZL1 | Shunt Reactor | 1 | 1 | 60,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 263
264 | LOL_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 264
268 | MAL_400_REVZL1 | Shunt Reactor | 25 | 13 | 5,60 | 0,00 | 400 | Yes | 1,01 | 1,04 | 268
269 | MES_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 269
278 | NSP_150-ZL31 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 278
281 | NVV_150-ZL1 | Shunt Reactor | 1 | 1 | 80,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 281
286 | REV_400-ZL1- | Shunt Reactor | 25 | 13 | 5,60 | 0,00 | 400 | Yes | 1,01 | 1,04 | 286
288 | RSL_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 288
289 | RYT_150-ZL2 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 289
294 | SHE_150-ZL1 | Shunt Reactor | 18 | 1 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 294
295 | SIN_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 295
297 | STR_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 297
297 | STR_150-ZL2 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 297
311 | TJE_150-ZL1- | Shunt Reactor | 1 | 1 | 80,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 311
316 | TJE_400-ZL1 | Shunt Reactor | 1 | 1 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 316
316 | TJE_400-ZL2 | Shunt Reactor | 1 | 0 | 70,00 | 0,00 | 420 | Yes | 1,01 | 1,04 | 316
316 | TJE_400-ZL4 | Shunt Reactor | 25 | 13 | 5,60 | 0,00 | 400 | Yes | 1,01 | 1,04 | 316
321 | TRI_150-ZL1 | Shunt Reactor | 18 | 9 | 5,58 | 0,00 | 165 | Yes | 0,97 | 1,01 | 321
322 | TRI_220-ZL1 | Shunt Reactor | 25 | 14 | 5,60 | 0,00 | 235 | Yes | 0,00 | 1,05 | 322
322 | TRI_220-ZL2 | Shunt Reactor | 25 | 13 | 4,80 | 0,00 | 235 | Yes | 0,00 | 1,05 | 322
323 | TRI_400-ZL2 | Shunt Reactor | 1 | 1 | 141,12 | 0,00 | 420 | Yes | 1,01 | 1,04 | 323
326 | VHA_150-ZL31 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 326
327 | VHA_400-ZL1 | Shunt Reactor | 1 | 1 | 58,93 | 0,00 | 420 | Yes | 1,01 | 1,04 | 327
335 | VID_150-ZL1 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 335
339 | ÅBØ_150-ZL31 | Shunt Reactor | 1 | 1 | 40,00 | 0,00 | 165 | Yes | 0,97 | 1,01 | 339
340 | ÅSP_150-ZL1 | Shunt Reactor | 1 | 1 | 60,00 | 0,00 | 170 | Yes | 0,97 | 1,01 | 340

## HVDC
HVDC Data | Energinet.dk | 2020
Bus Index | HVDC Name | Pmax[MW] | Q[Mvar] | Act.P[MW] | Act.Q[Mvar]
11 | dc_CO1_EDR_400 | 700 | 1 | 546 | 1
12 | dc_KO1_BJS_400 | 350 | -270 | 350 | -270
13 | dc_KS1_XVH_ST31 | -360 | -182 | -295 | -149
14 | dc_KS2_XVH_LI11 | -360 | -173 | -295 | -141
15 | dc_SB1_XFG_HK11 | -600 | -270 | 0 | 0
16 | dc_SB1_XFG_HK12 | 600 | -270 | 0 | 0
17 | dc_SK1_XKR_TJ31 | -250 | -165 | -137 | -90
18 | dc_SK2_XKR_TJ32 | -250 | -165 | -137 | -90
19 | dc_SK3_XKR_TJ13 | -500 | -225 | -400 | -180
20 | dc_SK4_XKR_TJ34 | -700 | 1 | 0 | 0
191 | dc_VL1_REV_400 | 1 | 1 | 0 | 0

## PFModelInfo
ELvis_TYNDP2016_ENTSOE_EP2020 | DK NUP EP2020-ENTSOE_ | Version_20160121_0714_PubRef | 2020-01-01/00:00:38